## Front & Preliminaries
|  |  |  | SPECIFICATION | OCTOBER
|  |  |  | S-620D | 2018
Data Sheets for
High-voltage switchgear and controlgear
Revision history
| VERSION | DATE | AMENDMENTS
| 1.0 | October 2018 | Issued for Publication
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Project 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-620D Data Sheets for
High-voltage switchgear and controlgear
Foreword
This specification package was prepared under a Joint Industry Project 33 (JIP33) “Standardization of Equipment Specifications for Procurement” organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Ten key oil and gas companies from the IOGP membership participated in developing this specification under JIP33 Phase 2 with the objective to leverage and improve industry level standardization for projects globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, based on the ten participating members’ company specifications, resulting in a common and jointly approved specification, and building on recognized industry and/or international standards.
The specification package has been developed in consultation with a broad user and supplier base to promote the opportunity to realize benefits from standardization and achieve significant cost reductions for upstream project costs. The JIP33 work groups performed their activities in accordance with IOGP’s Competition Law Guidelines (November 2014).
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The vision from the CPC industry is to standardize specifications for global procurement for equipment and packages, facilitating improved standardization of major projects across the globe. While individual oil and gas companies have been improving standardization within their own businesses, this has limited value potential and the industry lags behind other industries and has eroded value by creating bespoke components in projects.
The specification package aims to significantly reduce this waste, decrease project costs and improve schedule through pre-competitive collaboration on standardization.
Following agreement of the relevant JIP33 work group and approval by the JIP33 Steering Committee, the IOGP Management Committee has agreed to the publication of this specification package by IOGP. Where adopted by the individual operating companies, the specification package aims to supersede existing company documentation for the purpose of industry-harmonized standardization.
IOGP S-620D Version 1.0
S-620D Data Sheets for
High-voltage switchgear and controlgear
Introduction
The purpose of this equipment datasheet is to define buyer specific requirements for the supply of high-voltage switchgear and controlgear in accordance with IEC 62271-200 for application in the petroleum and natural gas industries. The datasheet provides project specific requirements where the supplementary specification and its parent standard require the user to define an application specific requirement. It follows the clause structure of the parent standard (IEC 62271-200:2011) and the supplementary requirements specification (IOGP S-620). It also includes information required by the user for technical evaluation purposes. Additional user supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This datasheet shall be used in conjunction with the supplementary requirements specification, information requirements specification (IOGP S-620L) and quality requirements specification (IOGP S-620Q) which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheets
IOGP S-620D Version 1.0

## Guidance
S-620D Data Sheets for High-voltage switchgear and controlgear
Guidance on the use of these data sheets
To be used in conjunction with :
IOGP S-620
IEC 62271-200 Edition 2.0:2011
IEC 62271-1 Edition 2.0:2017
The contents of these Data Sheets are in strict sequence of the clause numbering in IEC 62271-200 and additions in IOGP S-620.
If Users need to add data items, these should be inserted as new rows within the clause numbering sequence.
In its original format, this document contains no hidden rows or columns, no locked or protected cells, no macros and limited conditional formatting.
In its original format, only document details on the cover sheet are referenced into the subsequent data sheets.
Users may add enhanced functionally to these Data Sheets to suit their work processes or project requirements.
For input data items, these Data Sheets contain drop down pick lists of IEC preferred values or IOGP default values.
For input data items, these Data Sheets contain cell comments explaining IEC preferred values or IOGP default values.
IOGP Specification default values are pre-populated into these data sheets, but may be modified as required by the User.
Additional user supplied documents as listed in the data sheets (Supplement tab), to define scope and technical requirements for enquiry and purchase of high-voltage switchgear and controlgear assemblies include (but not limited to):
| - | high-voltage switchgear and controlgear assemblies scope (equipment quantities/tag numbers, special tools, spare parts, services);
| - | user diagram(s), such as switchgear single line diagrams, and circuit and wiring diagrams;
| - | high-voltage switchgear and controlgear assemblies circuit schedule, or data file containing this information (one per assembly).
Where column B is populated with '104', this denotes that the parameter is detailed in IEC 62271-200 Table 104 - Summary of technical requirements, ratings and optional tests for metal-enclosed switchgear.
An example cover sheet has been provided, but Users may replace this sheet with alternative User format or project format.
An example Supplementary Requirements sheet has been provided. Users may delete or modify this sheet as required.
This document is originally formatted for print-out on A4 Portrait (210mm x 298mm) paper, with a scaling of 90% of normal size.
In its original 1.71 column width and 13.75 row height format, these cells print out as squares.
Sheets with Green colured tabs are those which shall be issued to suppliers
Sheets with Red tabs are for user / buyer information only
IOGP S-620D Version 1.0

## Cover
Insert Buyer Logo Here |  |  |  | S-620D Data Sheets for High-voltage switchgear and controlgear |  |  | Insert Project Logo Here
| CLIENT: |  |  |  | Insert Client_name
| PROJECT TITLE: |  |  |  | Insert Project Title
| PROJECT LOCATION: |  |  |  | Insert Project_location
| JOB/PROJECT NUMBER: |  |  |  | Insert Job/Project number
| HIGH-VOLTAGE SWITCHGEAR TAG NUMBER: |  |  |  | Insert Tag_No
| HIGH-VOLTAGE SWITCHGEAR SERVICE: |  |  |  | Insert Service Description
| CONFORMITY ASSESSMENT SYSTEM: |  |  |  | Insert required CAS level per QRS | [5 empty] | Select | A | B | C | D
| DOCUMENT NUMBER: |  |  |  | Insert Project Document Number
| REVISION: |  |  |  | Insert Project Document Revision
Issue |  | Date | Issue Description |  |  | By |  | Checked | Approved
IOGP S-620D Version 1.0 | [8 empty] | Sheet 1 of | 7
Note on U16: Optional Text : Intended for service description such as "Water Treatment Area 400V Switchboard"
Note on U18: Select CAS level per IOGP S-620Q (Quality Requirements Specification)
Note on U20: Author: Project Specific document number and format
Note on U22: Author: Project specification Revision number and format

## Sheet 2
Row |  | S-620D Data Sheets for High-voltage switchgear and controlgear | [13 empty] | Issue
2 |  | High-voltage Switchgear Tag No. : |  |  | Insert Tag_No
3 |  | High-voltage Switchgear Service : |  |  | Insert Service Description
4 |  | Ref. Clause | Characteristics |  |  |  |  | Requirement |  |  |  | Additional notes |  |  |  |  | Default
5 | 2 Normal and special service conditions
6 |  | 2.1.2 Indoor switchgear and controlgear
7 |  | 2.1.2 a) 1) | Ambient air temperature - Upper limit: |  |  |  |  | + 40 °C |  |  |  | Not exceeding this value |  |  |  |  | + 40 °C
8 |  | 2.1.2 a) 2) | Ambient air temperature - Daily average maximum: |  |  |  |  | + 35 °C |  |  |  | Not exceeding this value |  |  |  |  | + 35 °C
9 |  | 2.1.2 a) 3) | Ambient air temperature - Lower limit: |  |  |  |  | - 5 °C |  |  |  | Not exceeding this value |  |  |  |  | - 5 °C
10 |  | 2.1.2 b) | Influence from solar radiation: |  |  |  |  | No influence | [8 empty] | No influence
11 |  | 2.1.2 c) | Altitude: |  |  |  |  | 1000 m |  |  |  | Not exceeding this value |  |  |  |  | 1000 m
12 |  | 2.1.2 d) | Site pollution severity class (SPS): |  |  |  |  | Very light | [8 empty] | Select | Very light | Light | Medium | Heavy | Very heavy
13 |  | 2.1.2 e) 1) | Humidity conditions - 24 h average relative humidity: | [6 empty] | 95 % |  | Not exceeding this value |  |  |  |  | 95 %
14 |  | 2.1.2 e) 2) | Humidity conditions - 24 h average water vapour pressure: | [6 empty] | 2.2 kPa |  | Not exceeding this value |  |  |  |  | 2.2 kPa
15 |  | 2.1.2 e) 3) | Humidity conditions - one month average relative humidity: | [6 empty] | 90 % |  | Not exceeding this value |  |  |  |  | 90 %
16 |  | 2.1.2 e) 4) | Humidity conditions - one month average water vapour pressure: | [6 empty] | 1.8 kPa |  | Not exceeding this value |  |  |  |  | 1.8 kPa
17 |  | 2.1.2 f) 1) | Exposure to abnormal vibrations: |  |  |  | Less than switchgear itself | [9 empty] | Select | Less than switchgear itself
18 |  | 2.1.2 f) 2) | Exposure to abnormal shock or earth tremors : |  |  |  | Less than switchgear itself | [9 empty] | Select | Less than switchgear itself | Zone 0 - no qualification | Seismic severity level 1 | Seismic severity level 2
19 |  | 2.1.2 f) 3) | Exposure to abnormal tilting : |  |  |  | No abnormal tilting | [9 empty] | Select | No abnormal tilting
20 |  | 2.1.2g) 5.0.101 | Location environment: |  |  |  | Select | [9 empty] | Select | Onshore - Coastal | Onshore - Desert | Onshore - Industrial | Onshore - Inland | Offshore - Fixed | Offshore - Floating | Offshore - Mobile | Marine (Ship)
21 | 104 | 2 | Design class: |  |  |  | Class 0 | [9 empty] | Select | Class 0 | Class 1 | Class 2
22 |  | 2.1.3 Outdoor switchgear and controlgear
23 |  | 2.1.3 | Outdoor equipment requirements apply: |  |  |  | No, no outdoor equipment | [9 empty] | Select | No, no outdoor equipment | Yes, outdoor terminations
24 |  | 2.1.3 a) 1) | Ambient air temperature - Upper limit: |  |  |  |  | Not applicable |  |  |  | Not exceeding this value |  |  |  |  | Select | Not applicable | + 40 °C
25 |  | 2.1.3 a) 2) | Ambient air temperature - Daily average maximum: |  |  |  |  | Not applicable |  |  |  | Not exceeding this value |  |  |  |  | Select | Not applicable | + 35 °C
26 |  | 2.1.3 a) 3) | Ambient air temperature - Lower limit: |  |  |  |  | Not applicable |  |  |  | Not exceeding this value |  |  |  |  | Select | Not applicable | - 25 °C
27 |  | 2.1.3 b) | Influence from solar radiation: |  |  |  |  | Not applicable |  |  |  | Not exceeding this value |  |  |  |  | Select | Not applicable | 1000 W/m2
28 |  | 2.1.3 c) | Altitude: |  |  |  |  | Not applicable |  |  |  | Not exceeding this value |  |  |  |  | Select | Not applicable | 1000 m
29 |  | 2.1.3d) 5.114.3 | Site pollution severity class (SPS) : |  |  |  |  | Not applicable | [8 empty] | Select | Not applicable | Medium | Heavy | Very heavy
30 |  | 2.1.3 e) | Ice coating: |  |  |  |  | Not applicable |  |  |  | Not exceeding this value |  |  |  |  | Select | Not applicable | 20 mm
31 |  | 2.1.3 f) | Wind speed: |  |  |  |  | Not applicable |  |  |  | Not exceeding this value |  |  |  |  | Select | Not applicable | 34 m/s
32 |  | 2.1.3 g) | No outdoor equipment, outdoor service conditions not applicable | [13 empty] | Select | No outdoor equipment, outdoor service conditions not applicable | Average humidity values given in 2.1.2 e) may be exceeded. Condensation or precipitation may occur
33 |  | 2.1.3 h) | External vibrations or earth tremors: |  |  |  | Not applicable | [9 empty] | Select | Not applicable | Less than switchgear itself
34 |  | 2.2.7 Special service conditions - other parameters
35 |  | 2.2.7 a) | Values different to IEC 62271-1 default normal service conditions: | [6 empty] | Normal |  | See values in 2.1 above |  |  |  |  | Normal | Special
36 |  | 2.2.7 b) | Exceptional condensation liable to occur: | [6 empty] | Normal | [6 empty] | Normal | Special
37 |  | 2.2.7 c) | Heavy pollution of the air by: | [6 empty] | Normal | [6 empty] | Normal | Special
38 |  | 2.2.7 d) | Exposure to strong electric or magnetic fields: | [6 empty] | Normal | [6 empty] | Normal | Special
39 |  | 2.2.7 e) | Exposure to extreme climatic conditions: | [6 empty] | Normal | [6 empty] | Normal | Special
40 |  | 2.2.7 f) | Attack by fungus or small creatures: | [6 empty] | Normal | [6 empty] | Normal | Special
41 |  | 2.2.7 g) | Installation in location where fire or explosion hazards exist : | [6 empty] | Normal | [6 empty] | Normal | Special
42 |  | 2.2.7 h) | Exposure to heavy vibration, shocks, seismic occurrences: | [6 empty] | Normal | [6 empty] | Normal | Special
43 |  | 2.2.7 i) | Installation where current carrying/breaking capacity is affected: | [6 empty] | Normal | [6 empty] | Normal | Special
44 |  | 2.2.7 j) | Exposure to conducted and radiated disturbances: | [6 empty] | Normal | [6 empty] | Normal | Special
45 |  | 2.2.7 k) | Exceptional overvoltage conditions or voltage fluctuations: | [6 empty] | Normal |  | See values in 4.1 b) & c) below |  |  |  |  | Normal | Special
46 |  | 2.2.7 l) | Excessive harmonics in the supply voltage or load current: | [6 empty] | Normal |  | See THD value in 4.1 d) below |  |  |  |  | Normal | Special
47 |  | 2.2.7 m) | Exposure to contamination of air by sour gas (H2S) (SO2): | [6 empty] | Normal | [6 empty] | Normal | Special
48
49 | 4 Ratings
50 |  | 4.1 Rated voltage
51 | 104 | 4.1 a) | Rated voltage (Ur): | [5 empty] | Select | [7 empty] | Select | 3.6 kV | 7.2 kV | 12 kV | 17.5 kV | 24 kV | 36 kV | 40.5 kV | 52 kV | 4.76 kV | 8.25 kV | 15 kV | 15.5 kV | 25.8 kV | 27 kV | 38 kV | 48.3 kV
52 | 104 | 4.1 b) | Nominal system voltage: | [5 empty] | Select | [7 empty] | Select | 3.3 kV | 6.6 kV | 11 kV | 22 kV | 33 kV | 3 kV | 6 kV | 10 kV | 15 kV | 20 kV | 30 kV | 35 kV | 4.16 kV | 12.47 kV | 13.2 kV | 13.8 kV | 29.94 kV | 34.5 kV | 45 kV
53 | 104 | 4.1 c) | Number of phases: | [5 empty] | 3 phase | [7 empty] | 3 phase
54 | 104 | 8.104.6 | Type of system earthing: |  |  | Select | [10 empty] | Select | Solidly earthed neutral | Impedance earthed neutral | Isolated neutral
55 |  | 4.1 d) | Nominal system voltage variation: |  |  |  |  | +10 % |  | -10 % |  | Not exceeding these values |  |  |  |  | +10 % | -10 %
56 |  | 4.1 e) | Voltage transient variation with 1,5 s recovery time: |  |  |  |  | +15 % |  | -15 % |  | Not exceeding these values |  |  |  |  | +15 % | -15 %
57 |  | 4.1 f) | Maximum voltage variation: |  |  |  |  | +20 % |  | -20 % |  | Not exceeding these values |  |  |  |  | +20 % | -20 %
58 |  | 4.1 g) | Supply voltage harmonic content not exceeding: | [5 empty] | 6,5 % THD |  |  | Not exceeding this value |  |  |  |  | Select | 6,5 % THD | 5 % THD | 3 % THD
59 |  | 4.2 Rated insulation level
60 | 104 | 4.2 a) | Rated short-duration power-frequency withstand voltage (Ud): | [5 empty] | Select |  |  | Common/Across the isolating distance |  |  |  |  | Select | 10 / 12 | 20 / 23 | 28 / 32 | 38 / 45 | 50 / 60 | 70 / 80 | 80 / 90 | 95 / 110 | 19 / 21 | 36 / 40 | 50 / 55 | 60 / 66 | 70 / 77 | 80 / 88 | 95 / 105 | 105 / 115 | 120 / 132
61 | 104 | 4.2 b) | Rated lightning impulse withstand voltage (Up) kV peak: | [5 empty] | Select |  |  | Common/Across the isolating distance |  |  |  |  | Select | 20 / 23 | 40 / 46 | 60 / 70 | 75 / 85 | 95 / 110 | 125 / 145 | 145 / 165 | 170 / 195 | 185 / 215 | 250 / 290 | 19 / 21 | 36 / 40 | 50 / 55 | 60 / 66 | 70 / 77 | 80 / 88 | 95 / 105 | 105 / 115 | 120 / 132
62 |  | 4.2 | Main busbar insulation covering in air compartments: |  |  |  |  | Insulation covered | [8 empty] | Select | Insulation covered | Bare main busbars | Not applicable (GIS)
|  | DOCUMENT NUMBER : |  | Insert Project Document Number | [6 empty] | ISSUE : |  | Insert Project Document Revision | Sheet 2 of | 7 |  |  |  | `
Note on AO4: Note : Orange cells indicate data sheet pre-populated default values, to be retailed or modified by the user as required.
Note on W7: S-620 (1.0) 2.1.2 The normal service conditions as described in IEC 62271-1 Clause 4.1.2 shall be applied unless supplementary indoor special service conditions are defined as required by the user in the data sheets. Where offshore location is defined by the user in the data sheets, the maximum air temperature shall be 40 °C unless a higher figure of 45 °C is defined by the user in the data sheets. IEC 62271-1 (2.0) default Indoor : 40 °C. IOGP Comment Modify 40 °C value only if site conditions are higher than the IEC default value.
Note on AO7: Not exceeding this value
Note on W8: S-620 (1.0) 2.1.2 The normal service conditions as described in IEC 62271-1 Clause 4.1.2 shall be applied unless supplementary indoor special service conditions are defined as required by the user in the data sheets. IEC 62271-1 (2.0) default Indoor : 35 °C. IOGP Comment Modify 35 °C value only if site conditions are higher than the IEC default value.
Note on AO8: Not exceeding this value
Note on W9: S-620 (1.0) 2.1.2 The normal service conditions as described in IEC 62271-1 Clause 4.1.2 shall be applied unless supplementary indoorspecial service conditions are defined as required by the user in the data sheets. IEC 62271-1 (2.0) default Indoor : -5 °C. IOGP Comment Modify -5 °C value only if site conditions are colder than the IEC default value.
Note on AO9: Not exceeding this value
Note on W10: S-620 (1.0) 2.1.2 The normal service conditions as described in IEC 62271-1 Clause 4.1.2 shall be applied unless supplementary indoor special service conditions are defined as required by the user in the data sheets. IEC 62271-1 (2.0) default there is no influence from solar radiation
Note on W11: S-620 (1.0) 2.1.2 The normal service conditions as described in IEC 62271-1 Clause 4.1.2 shall be applied unless supplementary indoor specila service conditions are defined as required by the user in the data sheets. IEC 62271-1 (2.0) default does not exceed 1000 m IOGP Comment Modify 1000 m value only if site elevation is higher.
Note on AO11: Not exceeding this value
Note on W12: S-620 (1.0) 2.2.3 Exposure to pollution Unless exposed to polluting special service conditions as defined in the data sheets, high-voltage switchgear and controlgear assemblies shall be suitable for use in an indoor environment with a "very light" site pollution severity. IEC 62271-1 (2.0) 4.1.2 Default is "very light". d) the (indoor) ambient air is not significantly polluted by dust, smoke, corrosive and/or flammable gases, vapours or salt and would be considered as having site pollution severity class (SPS) "very light" according to IEC TS 60815-1:2008.
Note on Z13: S-620 (1.0) 2.1.2 The normal service conditions as described in IEC 62271-1 Clause 4.1.2 shall be applied unless supplementary indoor special service conditions are defined as required by the user in the data sheets. IEC 62271-1 (2.0) default the average value of the relative humidity, measured over a period of 24 h, does not exceed 95 %
Note on AO13: Not exceeding this value
Note on Z14: S-620 (1.0) 2.1.2 The normal service conditions as described in IEC 62271-1 Clause 4.1.2 shall be applied unless supplementary indoor special service conditions are defined as required by the user in the data sheets. IEC 62271-1 (2.0) default the average value of the water vapour pressure, over a period of 24 h, does not exceed 2.2 kPa
Note on AO14: Not exceeding this value
Note on Z15: S-620 (1.0) 2.1.2 The normal service conditions as described in IEC 62271-1 Clause 4.1.2 shall be applied unless indoor special service conditions are defined as required by the user in the data sheets. IEC 62271-1 (2.0) default the average value of the relative humidity, over a period of one month, does not exceed 90 %
Note on AO15: Not exceeding this value
Note on Z16: S-620 (1.0) 2.1.2 The normal service conditions as described in IEC 62271-1 Clause 4.1.2 shall be applied unless supplementary indoor special service conditions are defined as required by the user in the data sheets. IEC 62271-1 (2.0) default the average value of the water vapour pressure, over a period of one month, does not exceed 1.8 kPa
Note on AO16: Not exceeding this value
Note on G17: IOGP Comment IEC 62271-1 Clause 4.2.5 advises that standard switchgear and control gear is designed for mounting on substantially level structures free from excessive vibrations, shock or tilting without qualifying what is 'excessive'. For information: During development of IOGP S-620 it was identified that there is not a consensus of approach to defining vibration requirements or for switchgear testing, so it is necessary for the User to select the most appropriate standard or classification society requirements for a given installation. For offshore installations, a typical requirement is for electrical equipment and components to be constructed to withstand, without malfunctioning, or electrical connections loosening, vibrations in the frequency range 5 to 50 Hz with vibration velocity amplitude 20 mm/s. NOTE For guidance regarding sinusoidal vibration testing, see IEC 60068-2-6.
Note on U17: IEC 62271-1 (2.0) 4.1.2 f) Vibrations due to causes external to the switchgear and controlgear or earth tremors do not exceed the impact of vibrations caused by operation of the switchgear itself.
Note on G18: IOGP Comment IEC 62271-1 Clause 4.2.5 advises that standard switchgear and control gear is designed for mounting on substantially level structures free from excessive vibrations, shock or tilting without qualifying what is 'excessive'. For installations where earthquakes are likely to occur, IEC 62271-1 Clause 4.2.5 advises that the user should specify the operational requirements and the admissible damage level. For seismic testing, IEC 62271-1 Clause 4.2.5 makes reference to IEC 62271-207, IEC TS 62271-210, IEC TR 62271-300 and IEEE 693. The IEC/TS 62271-210 severity levels have been aligned with performance level according to IEEE 693. For information: During development of IOGP S-620 it was identified that there is not a consensus of approach to defining shock requirements or for switchgear testing, so it is necessary for the User to select the most appropriate standard or classification society requirements for a given installation. For offshore installations, a typical requirement is for electrical equipment and components to be constructed to withstand, without malfunctioning, or electrical connections loosening, peak accelerations ±0.6 g for offshore units of length exceeding 90 m (duration 5 to 10 s) and peak accelerations ±1 g for offshore units of length less than 90 m (duration 5 to 10 s). NOTE For guidance regarding shock testing, see IEC 60068-2-27.
Note on U18: IEC 62271-1 (2.0) 4.1.2 f) Vibrations due to causes external to the switchgear and controlgear or earth tremors do not exceed the impact of vibrations caused by operation of the switchgear itself.
Note on AQ18: IOGP Comment Switchgear qualified to IEC/TS 62271-210 Edition 1.0 Seismic qualification for metal enclosed and solid-insulation enclosed switchgear and controlgear assemblies for rated voltages above 1 kV and up to and including 52 kV. IEC/TS 62271-210 advises that for earthquake Zone 0, it is not necessary to perform any seismic qualification.
Note on AR18: IOGP Comment Switchgear qualified to IEC/TS 62271-210 Edition 1.0 Seismic qualification for metal enclosed and solid-insulation enclosed switchgear and controlgear assemblies for rated voltages above 1 kV and up to and including 52 kV. The severity level 1 is recommended for peak ground / floor accelerations up to 0,5 g. NOTE The severity level 1 is equivalent to the moderate performance level according to IEEE 693.
Note on AS18: IOGP Comment Switchgear qualified to IEC/TS 62271-210 Edition 1.0 Seismic qualification for metal enclosed and solid-insulation enclosed switchgear and controlgear assemblies for rated voltages above 1 kV and up to and including 52 kV. The severity level 2 is recommended for peak ground / floor accelerations up to 1,0 g. NOTE The severity level 2 is equivalent to the high performance level according to IEEE 693.
Note on G19: IOGP Comment IEC 62271-1 Clause 4.2.5 advises that standard switchgear and control gear is designed for mounting on substantially level structures free from excessive vibrations, shock or tilting without qualifying what is 'excessive'. IEC 61892-5 Section 5 defines limits of inclination for buoyant offshore units, aligned with the requirements of the MODU code. For information: The applied limits of inclination depend on the criticality of the installed equipment and the installation (vessel) type. Other inclination values may be accepted if justified by calculations for the particular offshore unit. National authorities may require larger inclinations.
Note on U19: IEC 62271-1 (2.0) 4.1.2 f) Vibrations due to causes external to the switchgear and controlgear or earth tremors do not exceed the impact of vibrations caused by operation of the switchgear itself.
Note on U20: S-620 (1.0) 2.1.2 Where offshore location is defined by the user in the data sheets, the maximum air temperature shall be 40°C unless a higher figure of 45°C is defined by the user in the data sheets. S-620 (1.0) 5.0.101 When marine class or offshore installation is identified by the user as a requirement in the data sheets, the equipment shall conform with the stated requirements for high-voltage switchgear and controlgear assemblies as defined in IEC 60092-101 and IEC 61892-3 respectively.
Note on AP20: IOGP Comment Definition of coastal environment contained within IEC TS 60815-1, but relates largely to the effect of pollution on outdoor insulator performance.
Note on AQ20: IOGP Comment Definition of desert environment contained within IEC TS 60815-1, but relates largely to the effect of pollution on outdoor insulator performance.
Note on AR20: IOGP Comment Definition of industrial environment contained within IEC TS 60815-1, but relates largely to the effect of pollution on outdoor insulator performance.
Note on AS20: IOGP Comment Definition of inland environment contained within IEC TS 60815-1, but relates largely to the effect of pollution on outdoor insulator performance.
Note on AT20: IOGP Comment Installations to IEC 61892 series except Part 6. Non-buoyant construction (platforms) engaged in offshore operations including drilling, production, storage or support functions, and which is designed and built for installation at a particular offshore location.
Note on AU20: IOGP Comment Installations to IEC 61892 series except Part 6. Buoyant construction (FPSOs etc.) engaged in offshore operations including production, storage or support functions, and which is designed and built for installation at a particular offshore location.
Note on AV20: IOGP Comment Installations to IEC 61892 series including Part 6. Buoyant construction engaged in offshore operations including drilling, production, storage, accommodation or support functions, not intended for service at one particular offshore site and which can be relocated without major dismantling or modification, e.g. barges, semisubmersible or jack-up unit and drill-ships.
Note on AW20: IOGP Comment Installations to IEC 60092 series.
Note on U21: IEC 62271-1 (2.0) 2 Metal enclosed switchgear and controlgear, under the scope of IEC/TS 62271-304 and intended to be used in service conditions more severe with respect to condensation and pollution than the normal service conditions specified in this standard, may be classified with a "design class" 1 or 2 according to IEC/TS 62271-304. IEC/TS 62271-304 (1.0) 3 Degree 0 corresponds to normal service conditions as described in 2.1.1 of IEC 62271-1.
Note on AP21: IEC/TS 62271-304 (1.0) 3 COPL Degree 0 corresponds to normal service conditions as described in 2.1.1 of IEC 62271-1. Co: Condensation does not normally occur (not more than twice a year) Equipment to be used in locations with humidity and/or temperature control in order to avoid condensation. The building or room provides protection from daily variations of outside climate. PL: Light pollution, the ambient air is not significantly polluted by dust, smoke, corrosive and/or flammable gases, vapours or salt. The manufacturer will assume that, in absence of specific requirements from the user, there are none. In order to reach light pollution in heavy polluted locations precautions may be necessary.
Note on AQ21: IEC/TS 62271-304 (1.0) 3 CLPL or COPH
Note on AR21: IEC/TS 62271-304 (1.0) 3 CLPH or CHPL or CHPH
Note on U23: S-620 (1.0) 2.1.3 If high-voltage bus duct runs that extend outdoors are required, the normal service conditions, as described in IEC 62271-1 Clause 4.1.3 shall be applied to the outdoor portion of bus ducts and outdoor bushings, unless supplementary outdoor special service conditions are defined as required by the user in the data sheets.
Note on W24: IEC 62271-1 (2.0) 4.1.3 a) Default is 40 °C
Note on AC24: Conditional formatting on this cell. "Not exceeding this value" is hidden if corresponding requirement is set to 'Not applicable'
Note on AQ24: Not exceeding this value
Note on W25: IEC 62271-1 (2.0) 4.1.3 a) Default is 35 °C
Note on AC25: Conditional formatting on this cell. "Not exceeding this value" is hidden if corresponding requirement is set to 'Not applicable'
Note on AQ25: Not exceeding this value
Note on W26: IEC 62271-1 (2.0) 4.1.3 a) Default is -25 °C
Note on AC26: Conditional formatting on this cell. "Not exceeding this value" is hidden if corresponding requirement is set to 'Not applicable'
Note on AQ26: Not exceeding this value
Note on W27: IEC 62271-1 (2.0) 4.1.3 b) Default is 1000 W/m2
Note on AC27: Conditional formatting on this cell. "Not exceeding this value" is hidden if corresponding requirement is set to 'Not applicable'
Note on AQ27: Not exceeding this value
Note on W28: IEC 62271-1 (2.0) 4.1.3 c) Default is not exceeding 1000 m
Note on AC28: Conditional formatting on this cell. "Not exceeding this value" is hidden if corresponding requirement is set to 'Not applicable'
Note on AQ28: Not exceeding this value
Note on W29: IEC 62271-1 (2.0) 4.1.3 Default is "Medium" d) the (outdoor) ambient air may be polluted by dust, smoke, corrosive gas, vapours or salt, the pollution does nor exceed site pollution severity class (SPS) "medium" as defined by IEC TS 60815-1:2008. S-620 (1.0) 5.114.3 Gas to air bushings Unless defined otherwise by the user in the data sheets, outdoor bushings shall be suitable for use in an outdoor environment with site pollution severity class (SPS) “medium” and selection to Approach 3 according to IEC TS 60815-1.
Note on W30: IEC 62271-1 (2.0) 4.1.3 e) Default is not exceeding 20 mm
Note on AC30: Conditional formatting on this cell. "Not exceeding this value" is hidden if corresponding requirement is set to 'Not applicable'
Note on AQ30: Not exceeding this value
Note on W31: IEC 62271-1 (2.0) 4.1.3 f) Default is 34 m/s
Note on AC31: Conditional formatting on this cell. "Not exceeding this value" is hidden if corresponding requirement is set to 'Not applicable'
Note on AQ31: Not exceeding this value
Note on U33: IEC 62271-1 (2.0) 4.1.3 f) vibrations due to causes external to the switchgear and controlgear or earth tremors do not exceed the impact of vibrations caused by operation of the switchgear itself.
Note on C34: S-620 (1.0) 2.2.7 High voltage switchgear and control gear shall be required to operate under parameters of special service conditions if defined by the User in the Data Sheets. Note The S-620D Data Sheet line items 2.2.7 a) to l) within section "Special service conditions - other parameters" align with the IEC 61439-1 [Clause 7.2] special service conditions requirements for LV switchgear and controlgear so that the HV and LV switchgear service conditions are defined in a similar manner. Item 2.2.7 m) has been added by IOGP to address sour gas field service conditions.
Note on Z35: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions.
Note on Z36: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions.
Note on Z37: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions.
Note on Z38: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions.
Note on Z39: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions.
Note on Z40: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions.
Note on Z41: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions.
Note on Z42: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions.
Note on Z43: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions.
Note on Z44: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions.
Note on Z45: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions.
Note on Z46: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions.
Note on Z47: IOGP Comment Default set at "Normal" If special service conditions are present, User to select "Special" and provide additional information on the prevailing conditions. No IEC definition to quantify at what concentrations of sour gas that the atmosphere becomes a Special Service Condition.
Note on Y51: IEC 62271-1 (2.0) 5.2.2 Range I for rated voltages of 245 kV and below Table 1, Series I: 3.6 kV upwards Table 2, Series II: 4.76 kV upwards
Note on Y52: IEC 60038 (7.0) 4.3 and 4.4 Nominal system voltages taken from Tables 3 and 4.
Note on AP52: IEC 60038 (7.0) from Table 3, Series I
Note on AQ52: IEC 60038 (7.0) from Table 3, Series I
Note on AR52: IEC 60038 (7.0) from Table 3, Series I
Note on AS52: IEC 60038 (7.0) from Table 3, Series I
Note on AT52: IEC 60038 (7.0) from Table 3, Series I
Note on AU52: IEC 60038 (7.0) from Table 3, Series I
Note on AV52: IEC 60038 (7.0) from Table 3, Series I
Note on AW52: IEC 60038 (7.0) from Table 3, Series I
Note on AX52: IEC 60038 (7.0) from Table 3, Series I
Note on AY52: IEC 60038 (7.0) from Table 3, Series I
Note on AZ52: IEC 60038 (7.0) from Table 3, Series I
Note on BA52: IEC 60038 (7.0) from Table 3, Series I
Note on BB52: IEC 60038 (7.0) from Table 3, Series II
Note on BC52: IEC 60038 (7.0) from Table 3, Series II
Note on BD52: IEC 60038 (7.0) from Table 3, Series II
Note on BE52: IEC 60038 (7.0) from Table 3, Series II
Note on BF52: IEC 60038 (7.0) from Table 3, Series II
Note on BG52: IEC 60038 (7.0) from Table 3, Series II
Note on BH52: IEC 60038 (7.0) from Table 4
Note on T54: IOGP Comment The type of system earthing affects the magnitude of maximum short-circuit current and single phase-to-earth arc fault current. See IEC 62271-200 Clauses 8.104.6 and 8.106 for further details.
Note on AC54: IOGP Comment For impedance earthed neutral, enter the type of impedance (e.g. Resistance, 400A 10 seconds) in the additional notes column.
Note on AQ54: IOGP Comment For impedance earthed neutral, enter the type of impedance (e.g. Resistance, 400A, 10 seconds) in the additional notes column.
Note on W55: IOGP comment Modify +10% value only if power supply system conditions are worse than this IEC default value.
Note on Z55: IOGP comment Modify -10% value only if power supply system conditions are worse than this IEC default value.
Note on W56: IOGP comment Modify +15% value only if power supply system conditions are worse than this IEC default value.
Note on Z56: IOGP comment Modify -15% value only if power supply system conditions are worse than this IEC default value.
Note on W57: IOGP comment Modify +20% value only if power supply system conditions are worse than this IEC default value.
Note on Z57: IOGP comment Modify -20% value only if power supply system conditions are worse than this IEC default value.
Note on Y58: S-620 (1.0) 4.1 Unless defined otherwise by the user in the data sheets, the high-voltage switchgear and controlgear assembly shall be suitable for operation with power system supply voltage harmonic content not exceeding 6,5% total harmonic distortion, without damaging effect. IOGP comment Modify 6,5% THD value only if power supply system conditions are worse than this default value.
Note on AP58: IEC TR 61000-3-6 (2.0) Table 2 - Indicative planning levels 1 kV < Un <= 35 kV, THD-MV 6,5 %
Note on AQ58: IEEE 519 (2014) Table 1 1 kV < V <= 69 kV THD 5 %
Note on AR58: IEC TR 61000-3-6 (2.0) Table 2 - Indicative planning levels 35 kV < Un <= 230 kV, THD-HV 3 %
Note on Y60: S-620 (1.0) 4.2 The rated insulation level of the high-voltage switchgear and controlgear shall be as defined by the user in the data sheets, selected from the Range I values given in Table 1 and Table 2 of IEC 62271-1. IEC 62271-1 (2.0) 5.3 Table 1 Rated insulation levels for rated voltages of range I, series I. Table 2 Rated insulation levels for rated voltages of range I, series II.
Note on AP60: IEC 62271-1 (2.0) Table 1 Rated voltage (Ur) : 3.6kV Corresponding lightning impulse withstand voltages (Up) : 20/23kV or 40/46kV
Note on AQ60: IEC 62271-1 (2.0) Table 1 Rated voltage (Ur) : 7.2kV Corresponding lightning impulse withstand voltages (Up) : 40/46kV or 60/70kV
Note on AR60: IEC 62271-1 (2.0) Table 1 Rated voltage (Ur) : 12kV Corresponding lightning impulse withstand voltages (Up) : 60/70kV or 75/85kV
Note on AS60: IEC 62271-1 (2.0) Table 1 Rated voltage (Ur) : 17.5kV Corresponding lightning impulse withstand voltages (Up) : 75/85kV or 95/110kV
Note on AT60: IEC 62271-1 (2.0) Table 1 Rated voltage (Ur) : 24kV Corresponding lightning impulse withstand voltages (Up) : 95/110kV or 125/145kV
Note on AU60: IEC 62271-1 (2.0) Table 1 Rated voltage (Ur) : 36kV Corresponding lightning impulse withstand voltages (Up) : 145/165kV or 170/195kV
Note on AV60: IEC 62271-1 (2.0) Table 1 Rated voltage (Ur) : 40.5kV Corresponding lightning impulse withstand voltages (Up) : 185/215kV
Note on AW60: IEC 62271-1 (2.0) Table 1 Rated voltage (Ur) : 52kV Corresponding lightning impulse withstand voltages (Up) : 250/290kV
Note on AX60: IEC 62271-1 (2.0) Table 2 Rated voltage (Ur) : 4.76kV Corresponding lightning impulse withstand voltages (Up) : 60/66kV
Note on AY60: IEC 62271-1 (2.0) Table 2 Rated voltage (Ur) : 8.25kV, 15kV or 15.5kV Corresponding lightning impulse withstand voltages (Up) : 95/105kV
Note on AZ60: IEC 62271-1 (2.0) Table 2 Rated voltage (Ur) : 15.5kV Corresponding lightning impulse withstand voltages (Up) : 110/121kV
Note on BA60: IEC 62271-1 (2.0) Table 2 Rated voltage (Ur) : 25.8kV or 27kV Corresponding lightning impulse withstand voltages (Up) : 125/138kV or 150/165kV
Note on BB60: IEC 62271-1 (2.0) Table 2 Rated voltage (Ur) : 27kV or 38kV Corresponding lightning impulse withstand voltages (Up) : 150/165kV
Note on BC60: IEC 62271-1 (2.0) Table 2 Rated voltage (Ur) : 38kV Corresponding lightning impulse withstand voltages (Up) : 170/187kV
Note on BD60: IEC 62271-1 (2.0) Table 2 Rated voltage (Ur) : 38kV Corresponding lightning impulse withstand voltages (Up) : 200/220kV
Note on BE60: IEC 62271-1 (2.0) Table 2 Rated voltage (Ur) : 48.3kV Corresponding lightning impulse withstand voltages (Up) : 250/275kV
Note on BF60: IEC 62271-1 (2.0) Table 2 Rated voltage (Ur) : 48.3kV Corresponding lightning impulse withstand voltages (Up) : 250/275kV
Note on Y61: S-620 (1.0) 4.2 The rated insulation level of high-voltage switchgear and controlgear shall be as defined by the user in the data sheets, selected from the Range I values given in Table 1 and Table 2 of IEC 62271-1. IEC 62271-1 (2.0) 5.3 Table 1 Rated insulation levels for rated voltages of range I, series I. Table 2 Rated insulation levels for rated voltages of range I, series II.
Note on AP61: IEC 62271-1 (2.0) Table 1 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 3.6kV
Note on AQ61: IEC 62271-1 (2.0) Table 1 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 3.6kV or 7.2kV
Note on AR61: IEC 62271-1 (2.0) Table 1 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 7.2kV or 12kV
Note on AS61: IEC 62271-1 (2.0) Table 1 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 12kV or 17.5kV
Note on AT61: IEC 62271-1 (2.0) Table 1 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 17.5kV or 24kV
Note on AU61: IEC 62271-1 (2.0) Table 1 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 24kV
Note on AV61: IEC 62271-1 (2.0) Table 1 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 36kV
Note on AW61: IEC 62271-1 (2.0) Table 1 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 36kV
Note on AX61: IEC 62271-1 (2.0) Table 1 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 40.5kV
Note on AY61: IEC 62271-1 (2.0) Table 1 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 52kV
Note on AZ61: IEC 62271-1 (2.0) Table 2 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 4.76kV
Note on BA61: IEC 62271-1 (2.0) Table 2 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 8.25kV, 15kV or 15.5kV
Note on BB61: IEC 62271-1 (2.0) Table 2 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 15.5kV
Note on BC61: IEC 62271-1 (2.0) Table 2 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 25.8kV or 27kV
Note on BD61: IEC 62271-1 (2.0) Table 2 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 27kV or 38kV
Note on BE61: IEC 62271-1 (2.0) Table 2 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 38kV
Note on BF61: IEC 62271-1 (2.0) Table 2 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 38kV
Note on BG61: IEC 62271-1 (2.0) Table 2 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 48.3kV
Note on BH61: IEC 62271-1 (2.0) Table 2 Rated lightning impulse withstand voltages (Up) for use with rated voltage (Ur) 48.3kV
Note on W62: S-620 (1.0) 4.2 Main busbars in air filled compartments and their branches to switching devices and voltage transformers, shall be insulation covered.

## Sheet 3
Row |  | S-620D Data Sheets for High-voltage switchgear and controlgear | [14 empty] | Issue
2 |  | High-voltage Switchgear Tag No. : |  |  | Insert Tag_No
3 |  | High-voltage Switchgear Service : |  |  | Insert Service Description
4 |  | Ref. Clause | Characteristics | [5 empty] | Requirement |  |  |  | Additional notes |  |  |  |  | Default
5 | 4 Ratings
6 |  | 4.3 Rated frequency
7 | 104 | 4.3 | Rated frequency (fr): | [7 empty] | Select | [6 empty] | Select | 50 Hz | 60 Hz
8 |  | 4.4 Rated normal current
9 |  | 4.4.1 | Conductor material of the assembly busbars: |  |  |  | In air/air mixture - copper | [10 empty] | Select | In air/air mixture - copper | Manufacturer's Standard
10 | 104 | 4.4.1 a) | Rated normal current of incomer functional units: | [5 empty] | See circuit schedule | [8 empty] | See circuit schedule
11 | 104 | 4.4.1 b) | Rated normal current of the assembly busbars (Ir): | [7 empty] | Select | [6 empty] | Select | 400 A | 500 A | 630 A | 800 A | 1000 A | 1250 A | 1600 A | 2000 A | 2500 A | 3150 A | 4000 A
12 | 104 | 4.4.1 c) | Rated normal current of feeder functional units: | [5 empty] | See circuit schedule | [8 empty] | See circuit schedule
13 |  | 4.5 Rated short-time withstand current
14 | 104 | 4.5.101 | Rated short-time withstand current (Ik): | [7 empty] | Select | [6 empty] | Select | 10 kA | 12.5 kA | 16 kA | 20 kA | 25 kA | 31.5 kA | 40 kA | 50 kA | 63 kA
15 | 104 | 4.5.102 | Rated short-time phase to earth withstand current (Ike): | [7 empty] | Select | [6 empty] | Select | 87% of Ik | 100% of Ik
16 |  | 4.6 Rated peak withstand current
17 | 104 | 4.6.101 | Rated peak withstand current (Ip): | [7 empty] | Select | [6 empty] | Select | 2.5 x Ik | 2.6 x Ik |  | 2.6 x Ik | 2.7 x Ik | 2.7 x Ik
18 | 104 | 4.6.102 | Rated peak phase to earth withstand current (Ipe): | [7 empty] | Select | [6 empty] | Select | 87% of Ip | 100% of Ip
19 |  | 4.7 Rated duration of short circuit
20 | 104 | 4.7.101 | Rated duration of short circuit (tk): | [7 empty] | 1 s | [6 empty] | Select | 1 s | 2 s | 3 s
21 | 104 | 4.7.102 | Rated duration of phase to earth short circuit (tke): | [7 empty] | 1 s | [6 empty] | Select | 1 s | 2 s | 3 s
22 |  | 4.8 Rated supply voltage of closing and opening devices and of auxiliary and control circuits
23 | 104 | 4.8 a) | Closing and tripping devices: | [7 empty] | Select | [6 empty] | Select | 24 V dc | 48 V dc | 60 V dc | 110 V dc | 125 V dc | 220 V dc | 250 V dc | 120 V ac | 220 V ac | 230 V ac | 240 V ac
24 | 104 | 4.8 b) | Indication: | [7 empty] | Select | [6 empty] | Select | 24 V dc | 48 V dc | 60 V dc | 110 V dc | 125 V dc | 220 V dc | 250 V dc | 120 V ac | 220 V ac | 230 V ac | 240 V ac
25 | 104 | 4.8 c) | Control: | [7 empty] | Select | [6 empty] | Select | 24 V dc | 48 V dc | 60 V dc | 110 V dc | 125 V dc | 220 V dc | 250 V dc | 120 V ac | 220 V ac | 230 V ac | 240 V ac
26 |  | 4.8 d) 5.108.2 | Circuit breaker spring charging motors: | [7 empty] | Select | [6 empty] | Select | 24 V dc | 48 V dc | 60 V dc | 110 V dc | 125 V dc | 220 V dc | 250 V dc | 120 V ac | 220 V ac | 230 V ac | 240 V ac
27 |  | 4.8 e) | Auxiliary circuits (e.g. panel lighting): | [7 empty] | Select | [6 empty] | Select | 110 V ac | 120 V ac | 220 V ac | 230 V ac | 240 V ac
28 |  | 4.9 Rated supply frequency of closing and opening devices and of auxiliary circuits (where a.c. is used)
29 | 104 | 4.9 | Rated supply frequency of auxiliary and control circuits: | [7 empty] | Select | [6 empty] | Select | 50 Hz | 60 Hz
30 |  | 4.101 Ratings of the internal arc classification (IAC)
31 | 104 | 4.101.2 5.101 | Accessibility type: | [7 empty] | Type A | [6 empty] | Select | Type A | Type B | Type C
32 | 104 | 4.101.3 5.101 | Classified sides: | [7 empty] | FLR | [6 empty] | Select | FLR | FL | FR
33 | 104 | 4.101.4 5.101 a) | Three-phase arc fault current ( IA ): |  |  |  | Not less than IK (4.5.101) | [10 empty] | Select | Not less than IK (4.5.101) | 10 kA | 12.5 kA | 16 kA | 20 kA | 25 kA | 31.5 kA | 40 kA | 50 kA | 63 kA
34 | 104 | 4.101.4 5.101 b) | Single phase-to-earth arc fault current ( IAe ): | [7 empty] | 87% of IA | [6 empty] | Select | 87% of IA
35 | 104 | 4.101.5 5.101 | Arc fault duration: | [7 empty] | 0,5 s | [6 empty] | Select | 0,5 s | 1 s
36 |  | 4.101.2.1 Equipment accessibility
37 |  | 4.101.2.1 a) | Back-to-wall switchgear configuration required: |  |  |  | Select | [10 empty] | Select | No | Yes | Manufacturer's standard
38 |  | 4.101.2.1 b) | Cable termination chamber location: |  |  |  | Select | [10 empty] | Select | Front access | Rear access | Manufacturer's standard
39 |  | 4.102 Rated cable test voltages
40 | 104 | 4.102.2 | Rated power-frequency cable test voltage Uct: |  |  |  | Select | [10 empty] | Select | Manufacturer's standard
41 | 104 | 4.102.3 | Rated d.c. cable test voltage Uct: |  |  |  | Select | [10 empty] | Select | Manufacturer's standard
42 | 5 Design and construction
43 | 104 | 5 | Main device type withdrawal requirements; |  |  |  | Manufacturer's standard | [10 empty] | Select | Manufacturer's standard | Withdrawable | Non-withdrawable | As per circuit schedule
44 |  | 5.0.101 General
45 |  | 5.0.101 | Mounting arrangement: |  |  | Longitudinal channels flush with the floor | [11 empty] | Select | Longitudinal channels flush with the floor | Directly bolted to the concrete floor | Mounted on elevated stanchions
46 |  | 5.0.102 Technology readiness and obsolescence
47 |  | 5.0.102 | Obsolescence management plan: |  |  |  | Manufacturer's standard | [10 empty] | Select | Manufacturer's standard | IEC 62402
48 |  | 5.0.103 Dependability of materials and parts
49 |  | 5.0.103 a) | Minimum service interval without busbar de-energization: | [6 empty] | 5 years | [7 empty] | Select | 4 years | 5 years | 6 years | 8 years | 10 years
50 |  | 5.0.103 b) | Minimum service interval for functional units: | [6 empty] | 5 years | [7 empty] | Select | 2 years | 4 years | 5 years | 6 years
51 |  | 5.2 Requirements for gases in switchgear and controlgear
52 |  | 5.2 | High-voltage compartment insulating medium: |  |  |  | Manufacturer's standard | [10 empty] | Select | Manufacturer's standard | Air | SF6 | Low GWP
53 |  | 5.3 Earthing of switchgear and controlgear
54 |  | 5.3.101 Earthing of the high-voltage conductive parts
55 |  | 5.3.101 a) | Classification of earthing switches for short-circuit making: | [6 empty] | E1 | [7 empty] | Select | E0 | E1 | E2
56 |  | 5.3.101 b) | Earthing switch mechanical endurance class: | [6 empty] | M0 | [7 empty] | Select | M0 | M1
57 |  | 5.3.101 c) | Earthing device operator location(s): |  |  |  | Select | [10 empty] | Select | Front of panel operation | Hand held umbilical device | Adjacent control panel | Remote operation
58 |  | 5.3.106 Voltage detecting and indicating systems
59 |  | 5.3.106 | Voltage detecting or indicating system provision: |  |  |  |  | Select | [9 empty] | Select | Not required | VDS to IEC 61243-5 | VPIS to IEC 62271-206
60
61
62
|  | DOCUMENT NUMBER : |  | Insert Project Document Number | [7 empty] | ISSUE : |  | Insert Project Document Revision | Sheet 3 of | 7 |  |  |  | `
Note on AO4: Note : Orange cells indicate data sheet pre-populated default values, to be retailed or modified by the user as required.
Note on Y7: IEC 62271-1 (2.0) 5.4 The preferred values of the rated frequency are 16,7Hz, 25Hz, 50Hz and 60Hz. IOGP Comment 16.7Hz and 25Hz not included in pick list as typically only used in railway traction systems.
Note on C8: S-620 (1.0) 4.4.2 Temperature rise The high-voltage switchgear and controlgear assembly shall comply with temperature rise limitations for the maximum design air temperature defined by the user in the data sheets.
Note on U9: S-620 (1.0) 4.4.1 Busbars in air insulated or gas-air mixture filled compartments shall be manufactured from hard drawn, high conductivity electrolytic copper unless aluminium is defined as required by the user in the data sheets. IOGP Comment Busbars in gas-filled compartments are routinely made of aluminium.
Note on Y11: IEC 62271-1 (2.0) 5.5 ..rated continuous current should be selected from the R10 series,
Note on Y14: IEC 62271-1 (2.0) 5.6 ..rated short-time withstand current should be selected from the R10 series..
Note on Y15: S-620 (1.0) 4.5.102 The value of rated short-time phase to earth withstand current (Ike) shall be at least 87% of the rated short-time withstand current (Ik) of the main circuit, unless defined otherwise by the user in the data sheets. IEC 62271-200 (2.0) 4.5.102 Rating assigned to the earthing circuit. This value may differ from that of the main circuit. IEC 62271-200 (2.0) 8.106 For systems with a solidly earthed neutral, the maximum short-circiut current of the earthing circuit may reach levels up to the rated short-time withstand current of the main circuit.
Note on Y17: IEC 62271-1 (2.0) 5.7 Table 5 Peak factors for rated peak withstand current. A DC time constant of 45 ms covers the majority of cases and corresponds to a rated peak withstand current equal to 2.5 times the rated short-time withstand current for a rated frequency of 50 Hz. For a rated frequency of 60 Hz, it is equal to 2.6 times the rated short-time withstand current.
Note on AP17: Frequency: 50 Hz DC time constant: 45 ms
Note on AQ17: Frequency: 60 Hz DC time constant: 45 ms
Note on AS17: Frequency: 50 Hz DC time constant: 60 ms
Note on AT17: Frequency: 50 Hz DC time constant: 75 ms and 120 ms
Note on AU17: Frequency: 60 Hz DC time constant: 60 ms, 75 ms and 120 ms
Note on Y18: S-620 (1.0) 4.6.102 The value of rated peak phase to earth withstand current (Ipe) shall be at least 87% of the rated peak withstand current (Ip) of the main circuit, unless defined otherwise by the user in the data sheets. IEC 62271-200 (2.0) 4.6.102 Rating assigned to the earthing circuit. This value may differ from that of the main circuit. IEC 62271-1 (2.0) 5.7 Table 5 Peak factors for rated peak withstand current. IEC 62271-200 (2.0) 8.106 For systems with a solidly earthed neutral, the maximum short-circiut current of the earthing circuit may reach levels up to the rated short-time withstand current of the main circuit. IEC 62271-102 (2.0) 5.101 The rated short-circuit making current is applicable only to the earthing switches class E1 and E2. This shall be equal to the rated peak withstand current.
Note on Y20: IEC 62271-1 (2.0) 5.8 The preferred value of rated duration of short-circuit is 1 s. IOGP Comment The IEC preferred value of 1 s is selected as the IOGP default minimum value. IEC 62271-1 (2.0) Clause 5.8 alternative lower value of 0.5 s is not included in IOGP pick list.
Note on Y21: S-620 (1.0) 4.7.102 The rated duration of phase to earth short circuit (tke) shall be equal to the rated duration of short circuit (tk) of the main circuit, unless defined otherwise by the user in the data sheets. IEC 62271-200 (2.0) 4.7.102 Rating assigned to the earthing circuit. This value may differ from that of the main circuit. IOGP Comment The IEC preferred value of 1 s is selected as the IOGP default minimum value. IEC 62271-1 (2.0) Clause 5.8 alternative lower value of 0.5 s is not included in IOGP pick list.
Note on Y23: S-620 (1.0) 4.8 The rated supply voltage of auxiliary and control circuits shall be as defined by the user in the data sheets, selected from the values given in Table 6 and from line items 1 to 5 in Table 7 of IEC 62271-1. S-620 (1.0) 5.113 Power supply for the protection relays shall be derived from the AC or DC tripping supply as defined by the user in the data sheets. IEC 62271-1 (2.0) 5.7.2 The rated supply voltage should be selected from the standard values given in Table 6 (DC) and Table 7 (AC). IOGP Comment 227V ac and 347V ac not included in IOGP pick list as not usual for IEC installations.
Note on Y24: S-620 (1.0) 4.8 The rated supply voltage of auxiliary and control circuits shall be as defined by the user in the data sheets, selected from the values given in Table 6 and from line items 1 to 5 in Table 7 of IEC 62271-1. IEC 62271-1 (2.0) 5.7.2 The rated supply voltage should be selected from the standard values given in Table 6 (DC) and Table 7 (AC). IOGP Comment 227V ac and 347V ac not included in IOGP pick list as not usual for IEC installations.
Note on Y25: S-620 (1.0) 4.8 The rated supply voltage of auxiliary and control circuits shall be as defined by the user in the data sheets, selected from the values given in Table 6 and from line items 1 to 5 in Table 7 of IEC 62271-1. IEC 62271-1 (2.0) 5.7.2 The rated supply voltage should be selected from the standard values given in Table 6 (DC) and Table 7 (AC). IOGP Comment 227V ac and 347V ac not included in IOGP pick list as not usual for IEC installations.
Note on Y26: S-620 (1.0) 5.108.2 Circuit-breaker operating mechanisms shall have: b) a spring charging motor operating at the voltage supply as defined by the user in the data sheets. S-620 (1.0) 4.8 The rated supply voltage of auxiliary and control circuits shall be as defined by the user in the data sheets, selected from the values given in Table 6 and from line items 1 to 5 in Table 7 of IEC 62271-1. IEC 62271-1 (2.0) 5.7.2 The rated supply voltage should be selected from the standard values given in Table 6 (DC) and Table 7 (AC). IOGP Comment 227V ac and 347V ac not included in IOGP pick list as not usual for IEC installations.
Note on Y27: S-620 (1.0) 4.8 The rated supply voltage of auxiliary and control circuits shall be as defined by the user in the data sheets, selected from the values given in Table 6 and from line items 1 to 5 in Table 7 of IEC 62271-1. IEC 62271-1 (2.0) 5.7.2 The rated supply voltage should be selected from the standard values given in Table 6 (DC) and Table 7 (AC). IOGP Comment 227V ac and 347V ac not included in IOGP pick list as not usual for IEC installations.
Note on Y29: IEC 62271-1 (2.0) 5.10 Where alternating current supply voltage is used, the preferred values of the rated supply frequency are 50Hz and 60Hz.
Note on Y31: S-620 (1.0) 4.101.2 Accessibility shall be Accessibility Type A unless defined otherwise by the user in the data sheets.
Note on AP31: IEC 62271-200 (2.0) 4.101.2 Accessibility Type A: restricted to authorized personnel only.
Note on AQ31: IEC 62271-200 (2.0) 4.101.2 Accessibility Type B: unrestricted accessibility, including that of the general public.
Note on AR31: IEC 62271-200 (2.0) 4.101.2 Accessibility Type C: restricted by installation out of reach and above a general public area.
Note on Y32: S-620 (1.0) 5.101 The internal arc classification (IAC) of the switchgear shall be FLR unless defined otherwise by the user in the data sheets.
Note on AP32: IEC 62271-200 (2.0) Annex AA FLR = Front, laterial and rear sides.
Note on AQ32: IEC 62271-200 (2.0) Annex AA FL = Front and laterial sides.
Note on AR32: IEC 62271-200 (2.0) Annex AA FR = Front and rear sides.
Note on U33: S-620 (1.0) 5.101 The internal arc type test for the high-voltage switchgear shall be for a rated three-phase arc fault current (IA) value not less than the defined rated short-time withstand current (Ik) for an arc fault duration of 0,5 s, unless defined for a longer duration by the user in the data sheets.
Note on Y34: IEC 62271-200 (2.0) 8.104.6 Table 103 Isolated neutral : up to 87% of the three-phase rated arc fault current Impedance earthed neutral : 100% of the rated single phase-to-earth arc fault current Soilidy eathed neutral : 100% of the three-phase rated arc fault current IOGP Comment IOGP default set at 100% of the three-phase rated arc fault current.
Note on Y35: S-620 (1.0) 5.101 The internal arc type test for the high-voltage switchgear shall be for a rated three phase arc fault current (IA) value not less than the defined rated short-time withstand current (Ik) for a minimum arc fault duration of 0,5 s, unless defined for a longer duration by the user in the data sheets. IOGP Comment The IEC standard recommended value of 0,1 s as detailed in IEC 62271-200 (2.0) Clause 4.101.5 has been deliberately excluded from the IOGP pick list.
Note on U37: S-620 (1.0) 4.101.2 All equipment shall be accessible from the front, except for cable termination chambers. Requirements for front or rear access to cable termination chambers shall be as defined by the user in the data sheets. All components in back-to-wall mounted high-voltage switchgear and controlgear assemblies shall be accessible from the front only.
Note on U38: S-620 (1.0) 4.101.2 All equipment shall be accessible from the front, except for cable termination chambers. Requirements for front or rear access to cable termination chambers shall be as defined by the user in the data sheets. All components in back-to-wall mounted high-voltage switchgear and controlgear assemblies shall be accessible from the front only.
Note on U40: IEC 62271-200 (2.0) 4.102.1 If switchgear is designed to allow the dielectric testing of cables while the cables are connected to the switchgear, one or more rated cable test voltages shall be assigned by the manufacturer. IEC 62271-200 (2.0) 8.107 Users should specify values of rated cable test voltages allowing adequate margins above the actual calbe test voltages expected to be applied.
Note on U41: IEC 62271-200 (2.0) 4.102.1 If switchgear is designed to allow the dielectric testing of cables while the cables are connected to the switchgear, one or more rated cable test voltages shall be assigned by the manufacturer. IEC 62271-200 (2.0) 8.107 Users should specify values of rated cable test voltages allowing adequate margins above the actual calbe test voltages expected to be applied.
Note on U43: IOGP Comment Table 104 within IEC 62271-200 has a user defined requirement option for "Withdrawable / non-withdrawable (main device type)". IOGP S-620 as no default position as to the main device type withdrawal requirements. AIS is more typically of withdrawable type and GIS is typically non-withdrawable type, but not exclusively so. IOGP default set at 'Manufacturer's standard', users to select an alternative if they have a preference.
Note on Q45: S-620 (1.0) 5.0.101 High-voltage switchgear and controlgear assemblies shall be suitable for securing to longitudinal runs of channels flush with the floor surface, unless defined otherwise by the user in the data sheets.
Note on U47: S-620 (1.0) 5.0.102 The manufacturer shall have an obsolescence management plan in accordance with a recognised system for all high-voltage switchgear and controlgear assembly components, as defined by the user in the data sheets. NOTE IEC 62402 is an example of an obsolesence management guide, refer to [17] of the Bibliography.
Note on X49: S-620 (1.0) 5.0.103 Unless longer service periods are defined as required by the user in the data sheets, high-voltage switchgear and controlgear assemblies and functional units shall be designed for continuous operation at full load under the normal service conditions for at least 45 000 hours (5 years). During this period, the main busbars and the distribution busbars (dropper system) shall not need to be de-energized for maintenance or inspection. The manufacturer shall identify components that are not suitable for 5 years continuous operation without inspection or replacement under the service conditions as defined in the data sheets.
Note on AR49: IOGP Comment Extended service period may require additional Manufacturer condition monitoring features.
Note on AS49: IOGP Comment Extended service period may require additional Manufacturer condition monitoring features.
Note on AT49: IOGP Comment Extended service period may require additional Manufacturer condition monitoring features.
Note on X50: S-620 (1.0) 5.0.103 Unless longer service periods are defined as required by the user in the data sheets, high-voltage switchgear and controlgear assemblies and functional units shall be designed for continuous operation at full load under the normal service conditions for at least 45 000 hours (5 years). During this period, the main busbars and the distribution busbars (dropper system) shall not need to be de-energized for maintenance or inspection. The manufacturer shall identify components that are not suitable for 5 years continuous operation without inspection or replacement under the service conditions as defined in the data sheets. S-620 (1.0) DD.5.0.103 With the exception of the replacement of interrupting elements, the manufacturer shall advise of any components requiring maintenance or inspection within the service periods defined, as required for the high-voltage switchgear by the user in the data sheets, that would require de-energizing of the main circuit of the fault current limiter assembly.
Note on AS50: IOGP Comment Extended service period may require additional Manufacturer condition monitoring features.
Note on U52: S-620 (1.0) 5.1 Liquids shall not be used as a switching or as an insulating medium unless agreed between the user and the manufacturer for use in specialist items. IOGP Comment While excluding the use of liquid (oil) as an insulating medium, S-620 is neutral on the type of air/gas used as an insulating medium. Users may have a technical preference or the need to specify equipment with a medium to match existing switchgear. Manufacturers may have hybrid construction designs, for example, using a different insulating medium for the busbar compartment compared to that being used in other high-voltage compartments.
Note on AS52: IOGP Comment GWP = Global Warming Potential SF6 alternatives, such as CO2, or proprietary alternatives with GWP significantly lower than the 23900 of SF6.
Note on X55: S-620 (1.0) 5.3.101 Switches for earthing of high-voltage conductive parts shall have a minimum classification for short-circuit making of Class E1, as specified in Clause 5.102 of IEC 62271 102 unless defined otherwise by the user in the data sheets. IEC 62271-102 (2.0) 5.101 The rated short-circuit making current is applicable only to the earthing switches class E1 and E2. This shall be equal to the rated peak withstand current.
Note on AP55: IEC 62271-102 (2.0) 5.102 E0 = Earthing switches with no making capability.
Note on AQ55: IEC 62271-102 (2.0) 5.102 E1 = Earthing switches with capability to withstand two short-circuit making operations.
Note on AR55: IEC 62271-102 (2.0) 5.102 E2 = Earthing switches with capability to withstand five short-circuit making operations.
Note on X56: S-620 (1.0) 5.3.101 Switches for earthing of high-voltage conductive parts shall have a minimum mechanical endurance Class M0, as specified in Clause 5.106 of IEC 62271-102 unless defined otherwise by the user in the data sheets.
Note on AP56: IEC 62271-102 (2.0) 5.106 M0 = 1000 operating cycles.
Note on AQ56: IEC 62271-102 (2.0) 5.106 M1 = 2000 operating cycles.
Note on U57: S-620 (1.0) 5.3.101 Earthing devices shall be arranged for manually initiated operation only, from operator locations as defined by the user in the data sheets.
Note on V59: S-620 (1.0) 5.3.106 Where defined as required by the user in the data sheets, a capacitive three-phase voltage detecting system to confirm the both the presence and absence of main circuit voltage in accordance with IEC 61243-5 shall be provided. The voltage detectors on each functional unit shall be installed adjacent to the connection (cable) compartment on all incoming circuits and outgoing feeders and on the front of the bus coupler panel(s) for each bus section. Where defined as required by the user in the data sheets, a capacitive three-phase voltage presence indicating system to confirm the presence of main circuit voltage in accordance with IEC 62271-206 shall be provided. The voltage indicators on each functional unit shall be installed adjacent to the connection (cable) compartment on all incoming circuits and outgoing feeders and on the front of the bus coupler panel(s) for each bus section.

## Sheet 4
Row |  | S-620D Data Sheets for High-voltage switchgear and controlgear | [15 empty] | Issue
2 |  | High-voltage Switchgear Tag No. : |  |  | Insert Tag_No
3 |  | High-voltage Switchgear Service : |  |  | Insert Service Description
4 |  | Ref. Clause | Characteristics | [7 empty] | Requirement |  |  | Additional notes |  |  |  |  | Default
5 | 5 Design and construction
6 |  | 5.4 Auxiliary and control equipment
7 |  | 5.4.1.2 Actuators and indication
8 |  | 5.4.1.2 a) | Discrete Indicator lamp type: |  |  | Long life LED |  |  |  |  | Indication colour :
9 |  | 5.4.1.2 b) | Circuit breaker closed (on): | [7 empty] | Red | [7 empty] | Red
10 |  | 5.4.1.2 c) | Circuit breaker open (off): | [7 empty] | Green | [7 empty] | Green
11 |  | 5.4.1.2 d) | Circuit breaker tripped: | [7 empty] | Yellow | [7 empty] | Yellow
12 |  | 5.4.1.2 e) | Circuit breaker trip circuit healthy (or unhealthy): | [7 empty] | Blue | [7 empty] | Blue
13 |  | 5.4.1.2 f) | Voltage indication (heater on): | [7 empty] | White | [7 empty] | White
14 |  | 5.4.1.2 g) | Motor running / contactor feeder on: | [7 empty] | Red | [7 empty] | Red
15 |  | 5.4.1.2 h) | Motor stopped / contactor feeder off: | [7 empty] | Green | [7 empty] | Green
16 |  | 5.4.1.2 i) | Motor starter / contactor feeder tripped: | [7 empty] | Yellow | [7 empty] | Yellow
17 |  | 5.4.1.2 j) | Motor heater on: | [7 empty] | White | [7 empty] | White
18 |  | 5.4.3.4.6 Heating elements
19 |  | 5.4.3.4.6 a) | LV auxiliary compartment heater provision: | [6 empty] | Select | [8 empty] | Select | Manufacturer's standard | Not required | Required
20 |  | 5.4.3.4.6 b) | HV connection compartment heater provision: | [6 empty] | Select | [8 empty] | Select | Manufacturer's standard | Not required | Required
21 |  | 5.4.3.4.6 c) | Switchgear compartment heater voltage: | [6 empty] | Select | [8 empty] | Select | 110 V ac | 120 V ac | 220 V ac | 230 V ac | 240 V ac
22 |  | 5.4.3.4.6 d) | Space heater control method: | [6 empty] | Manufacturer's standard | [8 empty] | Select | Manufacturer's standard | Thermostat | Hygrostat
23 |  | 5.4.3.4.6 e) | Remote motor space heater supply provision: | [6 empty] | Select | [8 empty] | Select | Not required | On all motors | As per circuit schedule
24 |  | 5.4.3.4.6 f) | Remote motor space heater supply voltage: | [6 empty] | Select | [8 empty] | Select | 110 V ac | 230 V ac | Not applicable
25 |  | 5.9 Low- and high-pressure interlocking and monitoring devices
26 |  | 5.9 | Method of local gas pressure indication/alarm: | [6 empty] | Manufacturer's standard | [8 empty] | Select | Manufacturer's standard | Sight gauge | Via IED display
27 |  | 5.15.1 Gas and vacuum tightness - General
28 |  | 5.15.1 | Circuit breaker switching medium: |  |  |  |  | Manufacturer's standard (not air) | [10 empty] | Select | Manufacturer's standard (not air) | Vacuum | SF6 | Low GWP | Air
29 |  | 5.15.1 | Contactor switching medium: |  |  |  |  | Manufacturer's standard (not air) | [10 empty] | Select | Manufacturer's standard (not air) | Vacuum | SF6 | Low GWP
30 |  | 5.15.2 Controlled pressure systems for gas
31 |  | 5.15.2 | Provision of controlled pressure systems: | [6 empty] | Not permitted | [8 empty] | Select | Not permitted | Permitted
32 |  | 5.17 Fire hazard (flammability)
33 |  | 5.17 | Resistance to abnormal heat and fire: | [5 empty] | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard | Low smoke, zero halogen
34 |  | 5.20.1 Protection against corrosion
35 |  | 5.20.1 a) | Protection against corrosion: | [6 empty] | Manufacturer's standard | [8 empty] | Select | Manufacturer's standard
36 |  | 5.20.1 b) | External surface finish colour: | [6 empty] | Manufacturer's standard | [8 empty] | Select | Manufacturer's standard | RAL 7035 Light Grey
37 |  | 5.102.1 Enclosure - General
38 |  | 5.102.1 a) | Consideration of floor surface: |  |  |  | Floor is not part of the enclosure | [11 empty] | Select | Floor is not part of the enclosure | Floor may be part of the enclosure
39 | 104 | 5.102.1 b) | Minimum degree of protection by enclosure with doors closed: | [8 empty] | IP3XW | [6 empty] | Select | IP3XW | IP31 | IP4XW | IP41
40 |  | 5.102.2 Covers and doors
41 |  | 5.102.2 c) | Door restraint (door stay) provision: | [5 empty] | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard | To be provided (floating/ship) | Required on LV compartments
42 | 104 | 5.102.2 d) | Main device compartment access: | [5 empty] | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard | Interlocked controlled | Procedure-based | Tool-based
43 | 104 | 5.102.2 e) | Cable HV terminal compartment access: | [5 empty] | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard | Interlocked controlled | Procedure-based | Tool-based
44 | 104 | 5.102.2 f) | Bus compartment access: | [5 empty] | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard | Interlocked controlled | Procedure-based | Tool-based
45 | 104 | 5.102.2 g) | Bus riser compartment access: | [5 empty] | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard | Interlocked controlled | Procedure-based | Tool-based
46 | 104 | 5.102.2 h) | Bus metering VT compartment access: | [5 empty] | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard | Interlocked controlled | Procedure-based | Tool-based
47 | 104 | 5.102.2 i) | Feeder/incomer VT compartment access: | [5 empty] | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard | Interlocked controlled | Procedure-based | Tool-based
48 | 104 | 5.102.2 j) | CT compartment access: | [5 empty] | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard | Interlocked controlled | Procedure-based | Tool-based
49 | 104 | 5.102.2 k) | LV/control compartment access: | [5 empty] | Tool or procedure-based | [9 empty] | Select | Tool or procedure-based | Tool-based | Procedure-based
50 |  | 5.102.2 l) | LV compartment doors: |  |  | Select | [12 empty] | Select | Manufacturer's standard locking facility | Padlockable, 6 mm hasp | Tumbler lock - common key | 7 mm square | 8 mm triangle | Double bit key No.5
51 |  | 5.102.2 m) | Safety shutters closed: |  |  | Manufacturer's standard locking facility | [12 empty] | Select | Manufacturer's standard locking facility | Padlockable, 8 mm hasp
52 |  | 5.102.2 n) | Disconnectors(isolators) open: |  |  | Manufacturer's standard locking facility | [12 empty] | Select | Manufacturer's standard locking facility | Padlockable, 8 mm hasp
53 |  | 5.102.2 o) | Earth switches open / closed: |  |  | Manufacturer's standard locking facility | [12 empty] | Select | Manufacturer's standard locking facility | Padlockable, 8 mm hasp
54 |  | 5.102.2 p) | Control selector switches: |  |  | Manufacturer's standard locking facility | [12 empty] | Select | Manufacturer's standard locking facility | Padlockable, 6 mm hasp
55 |  | 5.102.2 q) | Padlock provider: |  |  | Select | [12 empty] | Select | Not applicable | User supplied | Manufacturer supplied
56
57
58
59
60
61
62
|  | DOCUMENT NUMBER : |  | Insert Project Document Number | [8 empty] | ISSUE : |  | Insert Project Document Revision | Sheet 4 of | 7 |  |  |  | `
Note on AO4: Note : Orange cells indicate data sheet pre-populated default values, to be retailed or modified by the user as required.
Note on W8: S-620 (1.0) 5.4.1.2 On discrete indication components or on colour HMI screens, colour coding of status indication shall be in accordance with Table 105, unless defined otherwise by the user in the data sheets.
Note on U19: S-620 (1.0) 5.4.3.4.6 If defined as required by the user in the data sheets, low-voltage auxiliary and control component compartments and air insulated high-voltage connection (cable) compartments shall be provided with space heaters for anti-condensation prevention. IOGP Comment Some manufacturers do not advocate fitting heaters within low-voltage auxiliary compartments on the basis that the auxiliary components generate sufficient heat to protect against internal condensation.
Note on U20: S-620 (1.0) 5.4.3.4.6 If defined as required by the user in the data sheets, low-voltage auxiliary and control component compartments and air insulated high-voltage connection (cable) compartments shall be provided with space heaters for anti-condensation prevention.
Note on U21: S-620 (1.0) 5.4.3.4.6 Space heaters internal to the high-voltage switchgear and controlgear assemblies shall: - be designed for operation at the voltage as defined by the user in the data sheets; IEC 62271-1 (2.0) 5.7.2 The rated supply voltage should be selected from the standard values given in.... Table 7 (AC). IOGP Comment 227Vac and 347Vac not included in IOGP pick list as not usual for IEC installations.
Note on U22: S-620 (1.0) 5.4.3.4.6 The heating system of each bus section of the high-voltage switchgear and controlgear shall: - be controlled by a thermostat or hygrostat, as defined by the user in the data sheets;
Note on U23: S-620 (1.0) 5.4.3.4.6 If defined as required by the user in the data sheets, motor starter functional units shall be fitted with auxiliary circuits to supply remote space heaters within the high-voltage motors.
Note on U24: S-620 (1.0) 5.4.3.4.6 Auxiliary circuits for remote motor space heaters shall: - supply the motor space heaters at the voltage as defined by the user in the data sheets;
Note on U26: S-620 (1.0) 5.9 For GIS assemblies, local and remote indication and alarm capability shall be provided. The method of local pressure indication shall be as defined by the user in the data sheets.
Note on S28: S-620 (1.0) 5.15.1 For AIS assemblies, other than for earth switches and isolators, air shall not be used as a switching medium unless defined otherwise by the user in the data sheets.
Note on AS28: IOGP Comment GWP = Global Warming Potential SF6 alternatives, such as CO2, or proprietary alternatives with GWP significantly lower than the 23900 of SF6.
Note on S29: S-620 (1.0) 5.15.1 For AIS assemblies, other than for earth switches and isolators, air shall not be used as a switching medium unless defined otherwise by the user in the data sheets.
Note on AS29: IOGP Comment GWP = Global Warming Potential SF6 alternatives, such as CO2, or proprietary alternatives with GWP significantly lower than the 23900 of SF6.
Note on U31: S-620 (1.0) 5.15.2 For GIS assemblies, controlled pressure systems shall not be used unless defined otherwise by the user in the data sheets.
Note on T33: S-620 (1.0) 5.17 Where defined as required by the user in the data sheets, auxiliary and control circuit insulation shall be low smoke, zero halogen content.
Note on U35: S-620 (1.0) 5.20 Unless defined otherwise by the user in the data sheets, the Manufacturer’s standard painting and corrosion protection system for the service conditions defined in the data sheets shall be used.
Note on U36: S-620 (1.0) 5.20 Unless defined otherwise by the user in the data sheets, the Manufacturer's standard colour finish shall be used. IOGP Comment RAL 7035 appears to be the most prevalent colour provided as a manufacturer's standard.
Note on R38: S-620 (1.0) 5.102.1 The floor surface below the installed high-voltage switchgear and controlgear shall not be considered as being part of the enclosure unless defined otherwise by the user in the data sheets.
Note on Z39: S-620 (1.0) 5.102.1 When the metal enclosed high-voltage switchgear and controlgear is installed, the enclosure shall provide at least the degree of protection IP3XW. The supplementary “W” weather conditions shall be taken as water dripping from above the assembly. NOTE The supplementary “W” requirement is not subject to verification by testing.
Note on T41: S-620 (1.0) 5.102.2 Door restraints shall be provided for securing doors in the open position: - when defined as required by the user in the data sheets, on low-voltage compartment doors.
Note on T42: S-620 (1.0) 5.102.2 Covers or doors that give access to high-voltage compartments shall have accessibility as defined by the user in the data sheets.
Note on T43: S-620 (1.0) 5.102.2 Covers or doors that give access to high-voltage compartments shall have accessibility as defined by the user in the data sheets.
Note on T44: S-620 (1.0) 5.102.2 Covers or doors that give access to high-voltage compartments shall have accessibility as defined by the user in the data sheets.
Note on T45: S-620 (1.0) 5.102.2 Covers or doors that give access to high-voltage compartments shall have accessibility as defined by the user in the data sheets.
Note on T46: S-620 (1.0) 5.102.2 Covers or doors that give access to high-voltage compartments shall have accessibility as defined by the user in the data sheets.
Note on T47: S-620 (1.0) 5.102.2 Covers or doors that give access to high-voltage compartments shall have accessibility as defined by the user in the data sheets.
Note on T48: S-620 (1.0) 5.102.2 Covers or doors that give access to high-voltage compartments shall have accessibility as defined by the user in the data sheets.
Note on T49: S-620 (1.0) 5.102.2 Covers or doors that give access to compartments which do not contain any high-voltage parts (e.g. low-voltage control compartments, or mechanism compartments) shall have tool based or procedure based accessibility as defined by the user in the data sheets. NOTE Compartments secured by tumbler lock common keys or panel keys (e.g. 7 mm square, 8 mm triangle or similar) are regarded as procedure based access.
Note on Q50: S-620 (1.0) 5.102.2 Covers or doors that give access to compartments which do not contain any high-voltage parts (e.g. low-voltage control compartments, or mechanism compartments) shall have tool based or procedure based accessibility as defined by the user in the data sheets. NOTE Compartments secured by tumbler lock common keys or panel keys (e.g. 7 mm square, 8 mm triangle or similar) are regarded as procedure based access.
Note on AQ50: IOGP Comment Padlocking facilities, suitable for accepting padlocks with 6 mm hasp diameter minimum. Some manufacturer door cabinet handle designs cannot accept larger (8 mm) hasps.
Note on Q51: S-620 (1.0) 5.102.2 Covers and doors that are required to be locked to prevent access to live parts when the equipment is in operation shall facilitate padlocking.
Note on AQ51: IOGP Comment Padlocking facilities, suitable for accepting padlocks with 8 mm hasp diameter minimum and to also faciltiate use of multi-padlock holding LOTO devices.
Note on Q52: S-620 (1.0) 5.102.2 Covers and doors that are required to be locked to prevent access to live parts when the equipment is in operation shall facilitate padlocking.
Note on AQ52: IOGP Comment Padlocking facilities, suitable for accepting padlocks with 8 mm hasp diameter minimum and to also faciltiate use of multi-padlock holding LOTO devices.
Note on Q53: S-620 (1.0) 5.102.2 Covers and doors that are required to be locked to prevent access to live parts when the equipment is in operation shall facilitate padlocking.
Note on AQ53: IOGP Comment Padlocking facilities, suitable for accepting padlocks with 8 mm hasp diameter minimum and to also faciltiate use of multi-padlock holding LOTO devices.
Note on Q54: S-620 (1.0) 5.102.2 Covers and doors that are required to be locked to prevent access to live parts when the equipment is in operation shall facilitate padlocking.
Note on AQ54: IOGP Comment Padlocking facilities, suitable for accepting padlocks with 6 mm hasp diameter minimum. Some manufacturer standard selector switch designs cannot accept larger (8 mm) hasps.
Note on Q55: IOGP Comment Manufacturer should confirm dimensions for padlock hasp as part of their data submissions irrespective of who supplies the padlocks.

## Sheet 5
Row |  | S-620D Data Sheets for High-voltage switchgear and controlgear | [16 empty] | Issue
2 |  | High-voltage Switchgear Tag No. : |  |  | Insert Tag_No
3 |  | High-voltage Switchgear Service : |  |  | Insert Service Description
4 |  | Ref. Clause | Characteristics | [7 empty] | Requirement |  |  |  | Additional notes |  |  |  |  | Default
5 | 5 Design and construction
6 |  | 5.103.1 High-voltage compartments - General
7 | 104 | 5.103.1 | Loss of Service Continuity (LSC) category: |  |  |  |  | AIS - LSC2B/A, GIS - LSC2 | [11 empty] | Select | AIS - LSC2B/A, GIS - LSC2 | LSC1 | LSC2 | LSC2A | LSC2B
8 |  | 5.103.3.1 Partitions and shutters - General
9 | 104 | 5.103.3.1 a) | Partition class: | [5 empty] | Manufacturer's standard | [10 empty] | Select | Manufacturer's standard | PI not permitted
10 | 104 | 5.103.3.1 b) | Degree of protection by enclosure with doors open - partitions: | [9 empty] | IP2X | [6 empty] | Select | IP2X | IP2XC | IP3X | IP3XD
11 | 104 | 5.103.3.1 c) | Degree of protection by enclosure with doors open - shutters: | [9 empty] | IP2X | [6 empty] | Select | IP2X | IP2XC | IP3X | IP3XD
12 |  | 5.104 Removeable parts
13 |  | 5.104 | Facilities for remote testing of withdrawable units: | [8 empty] | Select | [7 empty] | Select | Not required | Required
14 |  | 5.106 Labelling and identification
15 |  | 5.106 a) | Main component, primary identification language: | [8 empty] | English | [7 empty] | English
16 |  | 5.106 b) | Main component, secondary identification language: | [8 empty] | Not required | [7 empty] | Not required
17 |  | 5.106.2 Identification of the conductors of main and auxiliary circuits :
18 |  | 5.106.2 a) | Phase 1 |  | L1 | [6 empty] | Brown | [7 empty] | L1 | Brown
19 |  | 5.106.2 b) | Phase 2 |  | L2 | [6 empty] | Black | [7 empty] | L2 | Black
20 |  | 5.106.2 c) | Phase 3 |  | L3 | [6 empty] | Grey | [7 empty] | L3 | Grey
21 |  | 5.106.2 d) | Neutral |  | N | [6 empty] | Blue | [7 empty] | N | Blue
22 |  | 5.106.2 e) | Protective earth |  | PE and/or earth symbol | [6 empty] | Yellow/Green | [7 empty] | PE and/or earth symbol | Yellow/Green
23 |  | 5.106.2 f) | DC positive pole |  | ( + ) | [6 empty] | Red | [7 empty] | ( + ) | Red
24 |  | 5.106.2 g) | DC negative pole |  | ( - ) | [6 empty] | White | [7 empty] | ( - ) | White
25 |  | 5.106.3 Mimic diagrams :
26 |  | 5.106.3 | Mimic (synoptic) diagrams: | [8 empty] | Not required | [7 empty] | Select | Not required | Required
27 |  | 5.108.1 Isolating switching devices (disconnectors)
28 |  | 5.108.1 a) | Switch electrical endurance class: | [8 empty] | Select | [7 empty] | Select | E1 | E2 | E3
29 |  | 5.108.1 b) | Switch mechanical endurance class: | [8 empty] | Select | [7 empty] | Select | M1 | M2
30 |  | 5.108.1 c) | Switch capacitive current breaking class: | [8 empty] | No classification | [7 empty] | Select | No classification | C1 | C2
31 |  | 5.108.2 Circuit-breakers
32 |  | 5.108.2 a) | Circuit-breaker electrical endurance class: | [8 empty] | E2 | [7 empty] | Select | E1 | E2
33 |  | 5.108.2 b) | Circuit-breaker restrike class: | [8 empty] | C1 | [7 empty] | Select | C1 | C2
34 |  | 5.108.2 c) | Circuit-breaker mechanical endurance class: | [8 empty] | M1 | [7 empty] | Select | M1 | M2
35 |  | 5.108.2 d) | Circuit-breaker system class: | [8 empty] | S1 | [7 empty] | Select | S1 | S2
36 |  | 5.108.2 e) | Minimum spare auxiliary contact provision : |  |  |  | 2 x 52a, 2 x 52b, 2 x in-service | [12 empty] | Select | 2 x 52a, 2 x 52b, 2 x in-service | 3 x 52a, 3 x 52b, 3 x in-service | 4 x 52a, 4 x 52b, 4 x in-service
37 |  | 5.109 Voltage transformers
38 |  | 5.109 a) | Secondary voltage: | [7 empty] | 110 V | [8 empty] | Select | 100 V | 110 V | 200 V | 120 V | 115 V | 230 V
39 |  | 5.111 Surge arrestors
40 |  | 5.111 | Provision of metal oxide surge arresters to IEC 60099-4: | [8 empty] | Select | [7 empty] | Select | Not required | Required
41 |  | 5.112 Indication and measuring devices
42 |  | 5.112.3 Digital instruments
43 |  | 5.112.3 | Multi-function digital measuring device accuracy: | [8 empty] | Class 1,0 S | [7 empty] | Select | Class 1,0 S | Class 0,5 S
44 |  | 5.112.4 Energy metering
45 |  | 5.112.4 | Static energy and maximum demand metering accuracy: | [8 empty] | Select | [7 empty] | Select | Class 1,0 S | Class 0,5 S
46 |  | 5.112.5 Transducer outputs
47 |  | 5.112.5 | Transducer output: | [6 empty] | 4-20 mA | [9 empty] | Select | 4-20 mA | 0-10 mA
48 |  | 5.113 Protection devices
49 |  | 5.113 | Protection relay type: |  |  | IED - User defined provider and range | [13 empty] | Select | IED - Manufacturer's standard | IED - User defined provider and range
50 |  | 5.113 | Auxiliary supply voltage variation: | [5 empty] | 85 % |  |  | to | 110 % |  | Not exceeding these values |  |  |  |  | 85 % | 110 %
51
52
53
54
55
56
57
58
59
60
61
62
|  | DOCUMENT NUMBER : |  | Insert Project Document Number | [9 empty] | ISSUE : |  | Insert Project Document Revision | Sheet 5 of | 7 |  |  |  | `
Note on AO4: Note : Orange cells indicate data sheet pre-populated default values, to be retailed or modified by the user as required.
Note on T7: S-620 (1.0) 5.103.1 For GIS assemblies, the LSC category shall be LSC2. For AIS assemblies, the LSC category shall be: - for circuit breaker functional units, LSC2B; - for contactor feeder functional units serving circuits without back-feed, a minimum of LSC2A.
Note on U9: IOGP Comment IOGP supplementary requirements do not stipulate on the class of partitions, permitting use of Manufacturer's standard, be it PM or PI.
Note on Z10: S-620 (1.0) 5.102.1 Partitions and shutters shall provide at least the degree of protection IP2X according to IEC 62271 1, Table 7, unless defined otherwise by the user in the data sheets.
Note on AQ10: IOGP Comment Enclosure protected against ingress to jointed finger 12mm diameter with 80 mm length and also protection against an access probe of 2.5mm diameters with 100mm length, both shall have adequate clearance from hazardous parts.
Note on AS10: IOGP Comment Enclosure protected against ingress a probe of 2.5mm diameter which shall not penetrate the enclosure and also against an access probe of 1.0mm diameter with 100mm length, which shall have adequate clearance from hazardous parts.
Note on Z11: S-620 (1.0) 5.102.1 Partitions and shutters shall provide at least the degree of protection IP2X according to IEC 62271 1, Table 7, unless defined otherwise by the user in the data sheets.
Note on AQ11: IOGP Comment Enclosure protected against ingress to jointed finger 12mm diameter with 80 mm length and also protection against an access probe of 2.5mm diameters with 100mm length, both shall have adequate clearance from hazardous parts.
Note on AS11: IOGP Comment Enclosure protected against ingress a probe of 2.5mm diameter which shall not penetrate the enclosure and also against an access probe of 1.0mm diameter with 100mm length, which shall have adequate clearance from hazardous parts.
Note on X13: S-620 (1.0) 5.104 Where defined as required by the user in the data sheets, facilities for remote testing of withdrawable main circuit units shall be provided by means of extension umbilicals or specific test modules.
Note on X15: S-620 (1.0) 5.106 The language used on all devices, labels, plates and notices shall be English, unless alternative or additional languages are defined as required by the user in the data sheets.
Note on X16: S-620 (1.0) 5.106 The language used on all devices, labels, plates and notices shall be English, unless alternative or additional languages are defined as required by the user in the data sheets.
Note on P18: S-620 (1.0) 5.106.2 The identification of the conductors of main and auxiliary circuits shall be in accordance with Table 107, unless defined otherwise by the user in the data sheets. AC Circuits, Phase 1 - L1 - Brown
Note on P19: S-620 (1.0) 5.106.2 The identification of the conductors of main and auxiliary circuits shall be in accordance with Table 107, unless defined otherwise by the user in the data sheets. AC Circuits, Phase 2 - L2 - Black
Note on P20: S-620 (1.0) 5.106.2 The identification of the conductors of main and auxiliary circuits shall be in accordance with Table 107, unless defined otherwise by the user in the data sheets. AC Circuits, Phase 3 - L3 - Grey
Note on P21: S-620 (1.0) 5.106.2 The identification of the conductors of main and auxiliary circuits shall be in accordance with Table 107, unless defined otherwise by the user in the data sheets. AC Circuits, Neutral - N - Blue
Note on P22: S-620 (1.0) 5.106.2 The identification of the conductors of main and auxiliary circuits shall be in accordance with Table 107, unless defined otherwise by the user in the data sheets. AC Circuits, Protective earth - PE and/or earth symbol - Yellow/Green
Note on P23: S-620 (1.0) 5.106.2 The identification of the conductors of main and auxiliary circuits shall be in accordance with Table 107, unless defined otherwise by the user in the data sheets. DC Circuits, Positive pole (+) - Red
Note on P24: S-620 (1.0) 5.106.2 The identification of the conductors of main and auxiliary circuits shall be in accordance with Table 107, unless defined otherwise by the user in the data sheets. DC Circuits, Negative pole (-) - White
Note on X26: S-620 (1.0) 5.106.3 If defined as required by the user in the data sheets, a durable mimic one-line (synoptic) diagram shall be provided on the front of the assembly, displaying the single line arrangement of busbars and the main circuit switching devices of incomers, bus couplers, feeders and starters. IOGP Comment "If defined as required" indicates an User option. Default position is "Not required".
Note on X28: S-620 (1.0) 5.108.1 Switches shall comply with IEC 62271-103. Electrical and mechanical endurance class shall be as defined by the user in the data sheets.
Note on AP28: IEC 62271-103 (1.0) 3.4.103.1 E1 = general purpose switch capable of performing a basic electrical endurance of load breaking currents and short-circuit makings.
Note on AQ28: IEC 62271-103 (1.0) 3.4.103.2 E2 = general purpose switch capable of performing a medium electrical endurance of load breaking currents and short-circuit makings.
Note on AR28: IEC 62271-103 (1.0) 3.4.103.3 E3 = general purpose switch capable of performing a high electrical endurance of load breaking currents and short-circuit makings.
Note on X29: S-620 (1.0) 5.108.1 Switches shall comply with IEC 62271-103. Electrical and mechanical endurance class shall be as defined by the user in the data sheets.
Note on AP29: IEC 62271-103 (1.0) 3.4.103.4 M1 = 1000 operating cycles.
Note on AQ29: IEC 62271-103 (1.0) 3.4.103.5 M2 = 5000 operating cycles.
Note on X30: S-620 (1.0) 5.108.1 Switches shall comply with IEC 62271-103. Electrical and mechanical endurance class shall be as defined by the user in the data sheets. IOGP comment No stated requirement for the capacitive current breaking class within S-620, hence default minimum is a general purpose switch.
Note on AP30: IEC 62271-103 (1.0) 3.4.103 General purpose switch.
Note on AQ30: IEC 62271-103 (1.0) 3.4.103.6 C1 = switch with capability of capacitive current breaking as demonstated by specific type tests.
Note on AR30: IEC 62271-103 (1.0) 3.4.103.7 C2 = switch with very low probability of restrike during capacitive current breaking as demonstated by specific type tests..
Note on X32: IOGP Comment Circuit breakers of rated voltage up to and including 52 kV have a default electrical endurance class of E2 in accordance with IEC 62271-100 (2.2) Clause 4.111.
Note on AP32: IEC 62271-101 (2.2) 3.4.112 E1 = Circuit-breaker with basic electrical endurance not falling into the category of class E2.
Note on AQ32: IEC 62271-100 (2.2) 3.4.113 E2 = Circuit-breaker designed so as not to require maintenance of the interrupting parts of the main circuit during its expected operating life, and only minimal maintenance of its other parts (circuit-breaker with extended electrical endurance).
Note on X33: IOGP Comment IOGP S-620 does not specify the restrike class so the IEC minimum is the default, which is Class C1. The main differences in restrike performances between class C1 and C2 type tests are the number of tests shots and the allowable number of restrikes.
Note on AP33: IEC 62271-100 (2.2) 3.4.114 C1 = Circuit-breaker with low probability of restrike during capacitive current breaking as demonstrated by specific type tests. IOGP Comment IEC TR 62271-306 advises that Class C1 is acceptable for medium voltage circuit-breakers and circuit-breakers applied for infrequent switching of transmission lines and cables.
Note on AQ33: IEC 62271-100 (2.2) 3.4.115 C2 = Circuit-breaker with very low probability of restrike during capacitive current breaking as demonstrated by specific type tests. IOGP Comment IEC TR 62271-306 advises that Class C2 is recommended for capacitor bank circuit-breakers and those used on frequently switched transmission lines and cables.
Note on X34: IOGP Comment IOGP S-620 does not specify the mechanical class so the IEC minimum is the default, which is Class M1.
Note on AP34: IEC 62271-100 (2.2) 4.110 M1 = Standard circuit-breaker with normal mechanical endurance of 2,000 operating sequences.
Note on AQ34: IEC 62271-100 (2.2) 4.110 M2 = Circuit-breaker for extended mechanical endurance of 10,000 operating sequences.
Note on X35: S-620 (1.0) 5.108.2 Circuit-breakers shall have a minimum of Class S1 intended for use with cable system circuits, unless defined otherwise by the user in the circuit schedule for line system circuits.
Note on AP35: IEC 62271-100 (2.2) 3.4.119 S1 = Circuit-breaker intended to be used in a cable system.
Note on AQ35: IEC 62271-100 (2.2) 3.4.120 S2 = Circuit-breaker used in a line- system.
Note on S36: S-620 (1.0) 5.108.2 Unless defined otherwise by the user in the data sheets, circuit-breakers shall have, as a minimum, the following spare volt free contacts wired to terminals in the outgoing terminal block: - Two normally open (52a) auxiliary contacts, - Two normally closed (52b) auxiliary contacts; and - For withdrawable circuit-breakers, two ‘in service’ position contacts.
Note on W38: S-620 (1.0) 5.109 VTs shall: a) have a secondary voltage of 110 V, unless defined otherwise by the user in the data sheets;
Note on AP38: Voltage from IEC 61869-3 (1.0) Clause 5.301.2
Note on AQ38: Voltage from IEC 61869-3 (1.0) Clause 5.301.2
Note on AR38: Voltage from IEC 61869-3 (1.0) Clause 5.301.2
Note on AS38: Voltage from IEC 61869-3 (1.0) Clause 5.301.2
Note on AT38: Voltage from IEC 61869-3 (1.0) Clause 5.301.2
Note on AU38: Voltage from IEC 61869-3 (1.0) Clause 5.301.2
Note on X40: S-620 (1.0) 5.111 Metal oxide surge arresters to IEC 60099-4, as required by the user in the data sheets, shall be installed on the circuit (cable) side of the main circuit switching device within a switchgear enslosure compartment.
Note on X43: S-620 (1.0) 5.112.3 Multi-function digital measuring devices shall have an accuracy class of 1,0 S unless defined otherwise by the user in the data sheets.
Note on X45: S-620 (1.0) 5.112.4 Static energy meters and maximum demand meters shall be in accordance with IEC 62052-11 with a default minimum accuracy class as defined by the user in the data sheets, or higher accuracy for specific schemes as defined in the user diagrams.
Note on V47: S-620 (1.0) 5.112.5 Unless defined otherwise by the user in the data sheets, the transducer outputs shall be 4–20 mA.
Note on Q49: S-620 (1.0) 5.113 Protection relays shall be of multi-function IED type unless defined otherwise by the user in the data sheets.
Note on U50: S-620 (1.0) 5.113 Protection relays shall maintain their accuracy and functionality for continuous operation at any point over the full range of AC and DC auxiliary voltage variations, defined by the user in the data sheets. IEC 62271-1 (2.0) 6.4.1 In case of electrical circuits it shall be possible to operate normally when the supply voltage measured at the supply terminals of the auxiliary and control circuits during operations is such that the voltage variation is within 85 % to 110 % of rated supply voltage (Ua). IOGP Comment Modify 85% value only if auxiliary power supply system conditions are worse than this default value.
Note on Z50: S-620 (1.0) 5.113 Protection relays shall maintain their accuracy and functionality for continuous operation at any point over the full range of AC and DC auxiliary voltage variations defined by the user in the data sheets. IEC 62271-1 (2.0) 6.4.1 In case of electrical circuits it shall be possible to operate normally when the supply voltage measured at the supply terminals of the auxiliary and control circuits during operations is such that the voltage variation is within 85 % to 110 % of rated supply voltage (Ua). IOGP Comment Modify 110% value only if auxiliary power supply system conditions are worse than this default value.

## Sheet 6
Row |  | S-620D Data Sheets for High-voltage switchgear and controlgear | [13 empty] | Issue
2 |  | High-voltage Switchgear Tag No. : |  |  | Insert Tag_No
3 |  | High-voltage Switchgear Service : |  |  | Insert Service Description
4 |  | Ref. Clause | Characteristics | [5 empty] | Requirement |  |  | Additional notes |  |  |  |  | Default
5 | 5 Design and construction
6 |  | 5.114 Cable terminations
7 |  | 5.114.1 Terminals for external conductors
8 |  | 5.114.1 a) | Incoming (supply) unit external conductor type: |  |  |  |  | Select | [8 empty] | Select | Cable - bolted lugs | Cable - separable system | Busbar trunking system
9 |  | 5.114.1 b) | Incoming (supply) unit direction of external conductors: | [5 empty] | From below | [7 empty] | Select | From below | From above
10 |  | 5.114.1 c) | Outgoing (load) unit external conductor type: |  |  |  |  | Select | [8 empty] | Select | Cable - bolted lugs | Cable - separable system
11 |  | 5.114.1 d) | Outgoing (load) unit direction of external conductors: | [5 empty] | From below | [7 empty] | Select | From below | From above
12 |  | 5.114.1 e) | External phase conductor, cross sections: |  |  |  |  | See Circuit Schedule | [8 empty] | Select | See Circuit Schedule
13 |  | 5.114.2 Terminals for control and auxiliaries
14 |  | 5.114.2 a) | Auxiliary cable direction of external conductors: | [5 empty] | From below | [7 empty] | Select | From below | From above
15 |  | 5.114.2 b) | Spare terminal provision for future use : | [5 empty] | None | [7 empty] | Select | None | 10 % space | 20 % space | 10 % spare | 20 % spare
16 |  | 5.115.1 Interface with supervisory systems
17 |  | 5.115.1 | Digital interface communications : |  |  | Select | [10 empty] | Select | Profinet | Modbus TCP/IP | IEC 61850 | Manufacturer's standard
18 |  | 5.115.4 Application of communication protocols to protective functions
19 |  | 5.115.4 a) | Conformance class : |  |  |  |  | Class c | [8 empty] | Select | Class a | Class b | Class c
20 |  | 5.115.4 b) | MICS : |  |  |  |  | Manufacturer to confirm | [8 empty] | Select | Manufacturer to confirm
21 |  | 5.115.4 c) | PICS : |  |  |  |  | Manufacturer to confirm | [8 empty] | Select | Manufacturer to confirm
22 |  | 5.115.4 d) | PIXIT : |  |  |  |  | Manufacturer to confirm | [8 empty] | Select | Manufacturer to confirm
23 |  | 5.115.4 e) | TICS : |  |  |  |  | Manufacturer to confirm | [8 empty] | Select | Manufacturer to confirm
24 |  | 5.115.4 f) | Number of redundant communication links : |  |  |  |  | Single | [8 empty] | Select | Single | Dual
25 |  | 5.115.4 g) | Timing performance : |  |  |  |  | Manufacturer to confirm | [8 empty] | Select | Manufacturer to confirm
26 |  | 5.115.4 h) | Availability class : |  |  |  |  | A2 | [8 empty] | Select | A1 | A2 | A3
27 |  | 5.115.4 i) | Maximum protection IEDs that controller subcribes to : | [5 empty] | Select | [7 empty] | Select | Manufacturer to specify
28
29 | 6 Dielectric tests
30 | 104 | 6.2.8 | Artificial pollution tests for outdoor insulators: |  |  |  | Not applicable | [9 empty] | Select | Not applicable | Not required | Required for outdoor bushings
31
32 | 7 Routine tests
33 | 104 | 7.101 | Partial discharge measurement test : |  |  |  |  | Not required | [8 empty] | Select | Not required | Required for GIS | Required for GIS and AIS
34 |  | 7.107 | ECMS simulation test : |  |  |  |  | Select | [8 empty] | Select | Not applicable | Not required | Required
35
36 | 9 Information to be given with enquiries, tenders and orders
37 |  | 9 | Language used for all provided information : | [6 empty] | English | [6 empty] | Select | English | User defined
38
39 | 10 Transport, storage, installation, operation and maintenance
40 |  | 10.1 Conditions during transport, storage and installation
41 |  | 10.1.1 | Storage environmental conditions : |  |  | Select | [10 empty] | Select | Within the normal service conditions | Within the special service conditions | See User requisition | See User packing specification
42 |  | 10.1.1 | Equipment integration location : |  |  | Select | [10 empty] | Select | Integration at User site | Integration not at end user site | See User integration specification
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
|  | DOCUMENT NUMBER : |  | Insert Project Document Number | [6 empty] | ISSUE : |  | Insert Project Document Revision | Sheet 6 of | 7 |  |  |  | `
Note on AO4: Note : Orange cells indicate data sheet pre-populated default values, to be retailed or modified by the user as required.
Note on U8: S-620 (1.0) 5.114.1 The default method of high-voltage cable termination for incoming circuits and outgoing circuits shall be as defined by the user in the data sheets, or if required differently for individual circuits, as defined in the circuit schedule.
Note on AQ8: IOGP Comment Such as vendor specific separable connector systems up to 36 kV in accordance with CENELEC HD 629.1 or separable insulated connector systems up to 35 kV in accordance with IEEE 386.
Note on W9: S-620 (1.0) 5.114.1 The default direction of entry for main circuit and auxiliary and control cables shall be from below unless defined otherwise by the user in the data sheets, or if required differently for individual circuits, as defined in the circuit schedule.
Note on U10: S-620 (1.0) 5.114.1 The default method of HV cable termination for incoming circuits and outgoing circuits shall be as defined by the user in the data sheets, or if required differently for individual circuits, as defined in the circuit schedule.
Note on AQ10: IOGP Comment Such as vendor specific separable connector systems up to 36 kV in accordance with CENELEC HD 629.1 or separable insulated connector systems up to 35 kV in accordance with IEEE 386.
Note on W11: S-620 (1.0) 5.114.1 The default direction of entry for main circuit and auxiliary and control cables shall be from below unless defined otherwise by the user in the data sheets, or if required differently for individual circuits, as defined in the circuit schedule.
Note on W14: S-620 (1.0) 5.114.1 The default direction of entry for main circuit and auxiliary and control cables shall be from below unless defined otherwise by the user in the data sheets, or if required differently for individual circuits, as defined in the circuit schedule.
Note on W15: S-620 (1.0) 5.114.2 If required by the user, space for, or provision of, unused spare terminals for future use shall be provided as defined by the user in the data sheets.
Note on R17: S-620 (1.0) 5.115.1 Communication interfaces with process control systems, ECMS or other non-safety function systems shall be as defined by the user in the data sheets.
Note on U19: IOGP Comment See IEC 62271-3 (1.0) Clause 9 Information to be given with enquiries, tenders and orders.
Note on AP19: IEC 62271-3 (2.0) 5.2.1 Class a is the minimal set of services required to operate switchgear, to allow very simple devices, i.e. "GOOSE-only-devices".
Note on AQ19: IEC 62271-3 (2.0) 5.2.1 Class b: the services required to implement the complete IEC 61850 series' data model with self-descriptive capabilities.
Note on AR19: IEC 62271-3 (2.0) 5.2.1 Class c: the implementation of all services that are applicable for the specific Logical Node. This includes configuration capabilities, file transfer and log.
Note on G20: IOGP Comment MICS = Model implementation conformance statement. See IEC 61850-10 (2.0) Clause 3.4.
Note on U20: IOGP Comment See IEC 62271-3 (1.0) Clause 9 Information to be given with enquiries, tenders and orders.
Note on G21: IOGP Comment PICS = Protocol implementation conformance statement. See IEC 61850-10 (2.0) Clause 3.6.
Note on U21: IOGP Comment See IEC 62271-3 (1.0) Clause 9 Information to be given with enquiries, tenders and orders.
Note on G22: IOGP Comment PIXIT = Protocol implementation extra information for testing. See IEC 61850-10 (2.0) Clause 3.7.
Note on U22: IOGP Comment See IEC 62271-3 (1.0) Clause 9 Information to be given with enquiries, tenders and orders.
Note on G23: IOGP Comment TICS = Technical issues conformance statement. See IEC 61850-10 (2.0) Clause 3.14.
Note on U23: IOGP Comment See IEC 62271-3 (1.0) Clause 9 Information to be given with enquiries, tenders and orders.
Note on U24: IOGP Comment See IEC 62271-3 (1.0) Clause 9 Information to be given with enquiries, tenders and orders.
Note on AP24: IOGP Comment IOGP S-620 5.108.2 g) 'Dual shunt trip coils' and 5.115.2 'Emergency shutdown interface relays' implies a hard wired solution for ESD trip functions but does not exclude the use of GOOSE messaging.
Note on AQ24: IEC 62271-3 (2.0) 6.1.3 For circuit breakers with multiple trip coils, redundancy in communications is required. IOGP Comment Dual redundancy is required if there are redundant protection schemes, each utilizing IEC 61850 messaging, not just because there are multiple trip coils as circuit breakers are sometimes fitted with dual trip coils as standard by the manufacturer.
Note on G25: IOGP Comment See IEC 62271-3 (2.0) Clause 5.3.
Note on U25: IOGP Comment See IEC 62271-3 (1.0) Clause 9 Information to be given with enquiries, tenders and orders.
Note on U26: IOGP Comment See IEC 62271-3 (1.0) Clause 9 Information to be given with enquiries, tenders and orders.
Note on AP26: IOGP Comment Availability class : A1 as per IEC 60870-4 A >= 99.00 %
Note on AQ26: IOGP Comment Availability class : A2 as per IEC 60870-4 A >= 99.75 %
Note on AR26: IOGP Comment Availability class : A3 as per IEC 60870-4 A >= 99.95 %
Note on W27: IOGP Comment See IEC 62271-3 (1.0) Clause 9 Information to be given with enquiries, tenders and orders.
Note on T30: S-620 (1.0) 6.2.8 Additional tests for condensation and pollution shall be performed if defined as required by the user in the data sheets.
Note on AP30: IOGP Comment De-select 'Not applicable' if there are outdoor bushings.
Note on U33: S-620 (1.0) 7.101 The partial discharge test shall be performed if defined as required by the user in the data sheets. IOGP Comment IOGP default set at "Not required". Partial discharge measurement is more appropriate for GIS.
Note on U34: S-620 (1.0) 7.107 Where defined by the user in the data sheets, a simulation test to validate the ECMS interfaces shall be carried out between the remote HMI and IEDs on the high-voltage switchgear and controlgear assemblies and the specific functions (remote control, restarting, automatic transfer, load shedding, etc.).
Note on X37: S-620 (1.0) 9 The language used for all provided information shall be English, unless defined otherwise by the user in the data sheets.
Note on R41: S-620 (1.0) 10.1.1 Preparation for shipment shall be in accordance with Manufacturer’s standard packing provision to meet project location and storage requirements as defined by the user in the data sheets and purchase order. IOGP Comment Any special transport or storage conditions, such as extended storage periods, or shock and vibration considerations, anticipated during transport should be defined by the user in the data sheets.
Note on R42: S-620 (1.0) 10.1.1 Where the equipment integration site differs from the end usage site, associated transport/logistic options and conditions at the integration site shall be subject to agreement between the user and the manufacturer. IOGP Comment For equipment integration other than at the intended service location, such as fabrication yards or shipyards, if the storage and installation conditions are more onerous than the normal service conditions, these conditions need to be identified.

## Supplement
Row | Note | S-620D Data Sheets for High-voltage switchgear and controlgear | [7 empty] | Issue
2
3 |  | High-voltage Switchgear Tag No. : |  |  | Insert Tag_No
4 |  | High-voltage Switchgear Service : |  |  | Insert Service Description
5
6 | USER SUPPLEMENTARY REQUIREMENTS
7 |  |  | Delete this sheet if not required.
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
|  | DOCUMENT NUMBER : |  | Insert Project Document Number |  | ISSUE : | Insert Project Document Revision | Sheet 7 of | 7