## Introduction
S-560D Data sheets for IEC 61439 - LV Switchgear and Controlgear Assemblies
Guidance on the use of these Data Sheets
To be used in conjunction with :
Specification S-560 Version 2.0
IEC 61439-1 Edition 2.0 2011
IEC 61439-2 Edition 2.0 2011
The contents of these Data Sheets are in strict sequence of the clause numbering in IEC 61439 and in the IOGP Specification.
If Users need to add data items, these should be inserted as rows within the clause numbering sequence.
In its original format, this document contains no hidden rows or columns, locked or protected cells, conditional formatting, or macros.
In its original format, only document details on the cover sheet are referenced into the subsequent data sheets.
Users may add enhanced functionally to these Data Sheets to suit their work processes or project requirements.
For input data items, these Data Sheets contain drop down pick lists of IEC preferred values or IOGP default values.
For input data items, these Data Sheets contain cell comments explaining IEC preferred values or IOGP default values.
IOGP Specification default values are pre-populated into these Data Sheets, but may be modified as required by the User.
An example cover sheet has been provided, but Users may replace this sheet with alternative User format or project format.
An example Supplementary Requirements sheet has been provided. Users may delete or modify this sheet as required.
An information sheet with PSC-Assembly examples has been provided. Users may delete this sheet if not required.
This document is originally formatted for print-out on A4 Portrait (210mm x 298mm) paper, with a scaling of 90% of normal size.
In its original 1.71 column width and 13.75 row height format, these cells print out as squares.
S-560D LV PSC-ASSEMBLY DATA SHEET Version 2.0

## Cover
S-560D Data sheets for IEC 61439 - LV Switchgear and Controlgear Assemblies
| CLIENT : |  |  | Client text here
| PROJECT TITLE : |  |  | Project text here
| PROJECT LOCATION : |  |  | Project location text here
| JOB/PROJECT NUMBER : |  |  | Job/Project number here
| PSC-ASSEMBLY TAG No. : |  |  | Tag No. number here
| PSC-ASSEMBLY SERVICE : |  |  | Sevice text here
| DOCUMENT NUMBER : |  |  | Data Sheet number here
| ISSUE : |  |  | XX
Aligned with Supplementary Requirements for IEC 61439 - LV Switchgear and Controlgear Assemblies S-560 Version 2.0
Aligned with IEC 61439 Low-voltage switchgear and controlgear assemblies -
Part 1: General rules, Edition 2.0 2011-08
Part 2: Power switchgear and controlgear assemblies, Edition 2.0 2011-08
Issue | Date |  | Issue Description |  | By | Checked | Approved
S-560D LV PSC-ASSEMBLY DATA SHEET Version 2.0 | [6 empty] | Sheet 1 of | 7
Note on N17: Optional Text : Intended for service description such as "Water Treatment Area 400V Switchboard"

## Sheet 2
Row |  | Data sheets for IEC 61439 - LV Switchgear and Controlgear Assemblies | [14 empty] | Issue
2 |  | PSC-Assembly Tag No. : |  | Tag No. number here
3 |  | PSC-Assembly Service : |  | Sevice text here
4 |  | Ref. Clause | Characteristics |  |  |  |  | Requirement |  |  |  |  | Additional notes
5 | 5 Interface Characteristics
6 |  | 5.1 General
7 |  | 5.1 a) | AC nominal supply voltage variation : |  |  |  |  | +10% |  |  | -10% |  | Not exceeding these values |  |  |  |  | +10% | -10%
8 |  | 5.1 b) | Frequency variation : |  |  |  |  | +5% |  |  | -5% |  | Not exceeding these values |  |  |  |  | +5% | -5%
9 | BB | 5.1 c), 9.1 | Temporary overvoltages : |  | Nominal system voltage + 1200 V | [12 empty] | Nominal system voltage + 1200 V
10 |  | 5.2 Voltage ratings
11 | BB | 5.2.1, 3.8.5 | Nominal voltage (of the electrical system) : |  |  |  |  | Select | [9 empty] | Select | 380V | 400V | 415V | 440V | 480V | 660V | 690V
12 | BB | 5.2.4 | Transient overvoltages, overvoltage category : |  |  |  |  | Category III | [9 empty] | Select | Category III | Category IV
13 |  | 5.3 Current ratings
14 | BB | 5.3.1 | Rated current of the assembly busbars (InA) : | [6 empty] | Select | [7 empty] | Select | 250 A | 315 A | 400 A | 500 A | 630 A | 800 A | 1000 A | 1250 A | 1600 A | 2000 A | 2500 A | 3150 A | 4000 A
15 | BB | 5.3.2 | Rated current of incoming functional unit circuits (Inc) : |  |  |  |  | See circuit schedule | [9 empty] | See circuit schedule
16 | BB | 5.3.2 | Rated current of outgoing functional unit circuits (Inc) : |  |  |  |  | See circuit schedule | [9 empty] | See circuit schedule
17 | BB | 3.8.7 | Prospective short-circuit current at supply terminals (Icp) : | [6 empty] | Input value | [7 empty] | Input value
18 |  | 5.3.4 | Rated short-time withstand current (Icw) : | [6 empty] | Select | [7 empty] | Select | 10 kA | 12.5 kA | 16 kA | 20 kA | 25 kA | 31.5 kA | 40 kA | 50 kA | 63 kA | 80 kA | 100 kA
19 |  | 5.3.4 | Rated short-time withstand current (Icw) time duration : | [6 empty] | Select | [7 empty] | Select | 0.2 s | 1 s | 3 s
20 |  | 5.3.3, 9.3.3 | Rated peak withstand current (Ipk) : | [6 empty] | Select | [7 empty] | Select | 17 kA | 25 kA | 32 kA | 40 kA | 52.5 kA | 66.15 kA | 84 kA | 105 kA | 138.6 kA | 176 kA | 220 kA | Special Condition | 25 kA | 31.5 kA | 40 kA | 50 kA | 63 kA | 80 kA | 100 kA | 125 kA | 160 kA | 200 kA | 250 kA
21 | BB | 5.3.5, 10.11 | Prospective short circuit current in the neutral : | [6 empty] | Max. 60% |  |  | % of rated Icp phase values |  |  |  |  | Select | Max. 60% | Max. 70% | Max. 80% | Max. 90% | Max. 100%
22 | BB | 5.3.4, 10.11 | Prospective short circuit current in the protective circuit : | [6 empty] | Max. 60% |  |  | % of rated Icp phase values |  |  |  |  | Select | Max. 60% | Max. 70% | Max. 80% | Max. 90% | Max. 100%
23 |  | 5.4 Rated diversity factor (RDF)
24 | BB | IEC 61439-2 | Assumed loading factor ;
25 |  | Table 101 | Section containing one functional unit : |  |  |  |  | 1.0 | [9 empty] | 1.0
26 |  |  | Distribution - 2 and 3 circuits : |  |  |  |  | 0.9 | [9 empty] | 0.9
27 |  |  | Distribution - 4 and 5 circuits : |  |  |  |  | 0.8 | [9 empty] | 0.8
28 |  |  | Distribution - 6 to 9 circuits : |  |  |  |  | 0.7 | [9 empty] | 0.7
29 |  |  | Distribution - 10 or more circuits : |  |  |  |  | 0.6 | [9 empty] | 0.6
30 |  |  | Electric actuator (MOV) : |  |  |  |  | 0.2 | [9 empty] | 0.2
31 |  |  | Motors rated less than or equal to 100 kW : |  |  |  |  | 0.8 | [9 empty] | 0.8
32 |  |  | Motors rated greater than 100 kW : |  |  |  |  | 1.0 | [9 empty] | 1.0
33 |  | 5.5 Rated frequency (fn)
34 | BB | 5.5 | Rated frequency (fn) : |  |  |  |  | Select | [9 empty] | Select | 50 Hz | 60 Hz | d.c.
35 |  | 5.6 Other characteristics (not defined elsewhere in these Data Sheets)
36 |  | 5.6 a) | Additional requirements depending on the specific service conditions of a functional unit (e.g. type of coordination, overload characteristics); |  |  |  | See circuit schedule | [10 empty] | See circuit schedule
37
38 |  | 5.6 c) | System configuration phases/wires : |  |  |  | 3-phase, 4-wire | [5 empty] | See also 8.6.1.1 'Neutral' |  |  |  |  | Select | 3-phase, 3-wire | 3-phase, 4-wire
39 | BB | 5.6 e), 3.5 | Stationary or movable : |  |  |  | Stationary | [10 empty] | Select | Stationary | Movable
40 | BB | 5.6 o) | Maximum overall dimensional requirements : |  |  | Manufacturer's standard | [11 empty] | Select | Manufacturer's standard | See packing specification
41 | BB | 5.6 p) | Maximum overall weight requirements : |  |  | Manufacturer's standard | [11 empty] | Select | Manufacturer's standard | See packing specification
42 | 6 Information
43 |  | 6.2.2 Information relating to the ASSEMBLY
44 |  | 6.2.1 | Language used for all provided information : | [5 empty] | English | [8 empty] | Select | English
45 |  | 6.2.2 Instructions for handling, installation, operation and maintenance (storage and handling)
46 | BB | 6.2.2 | Max. dimensions and weight of transport units : |  |  | Manufacturer's standard | [11 empty] | Select | Manufacturer's standard | See packing specification
47 | BB | 6.2.2 | Methods of transport : |  |  | Manufacturer's standard | [11 empty] | Select | Manufacturer's standard | See packing specification
48 | BB | 6.2.2 | Packing details : |  |  | Manufacturer's standard | [11 empty] | Select | Manufacturer's standard | See packing specification
49 |  | 6.3 Device and/or component identification
50 |  | 6.3 | Main component, primary identification language : | [5 empty] | English | [8 empty] | English
51 |  | 6.3 | Main component, secondary identification language : | [5 empty] | Not required | [8 empty] | Not required
52 |  | 6.3.101 | Synopic diagram | [5 empty] | Not required | [8 empty] | Not required
53
54
55
56
57
58
59
60
61
62
|  | DOCUMENT NUMBER : |  | Data Sheet number here | [7 empty] | ISSUE : |  | XX | Sheet 2 of | 7
Note on AO3: Note : Blue cells left blank for an additional User defined pick list entry.
Note on AO4: Note : Orange cells indicate data sheet default values, to be retailed or modified by the User as required.
Note on W7: S-560 (2.0) 5.1 Unless defined otherwise in the Data Sheets, the PSC-Assembly and ancillary components shall be suitable for operation without damaging effect, with power supply system variations of: a. AC/DC nominal supply voltage: ± 10%, S-560 comment Modify +10% value only if power supply system conditions are worse than this default value.
Note on Z7: S-560 (2.0) 5.1 Unless defined otherwise in the Data Sheets, the PSC-Assembly and ancillary components shall be suitable for operation without damaging effect, with power supply system variations of: a. AC/DC nominal supply voltage: ± 10%, Comment Modify -10% value only if power supply system conditions are worse than this default value.
Note on W8: S-560 (2.0) 5.1 Unless defined otherwise in the Data Sheets, the PSC-Assembly and ancillary components shall be suitable for operation without damaging effect, with power supply system variations of: b. Frequency: ± 5%, Comment Modify +5% value only if power supply system conditions are worse than this default value.
Note on Z8: S-560 (2.0) 5.1 Unless defined otherwise in the Data Sheets, the PSC-Assembly and ancillary components shall be suitable for operation without damaging effect, with power supply system variations of: b. Frequency: ± 5%, Comment Modify -5% value only if power supply system conditions are worse than this default value.
Note on S9: S-560 (2.0) 5.1 Unless defined otherwise in the Data Sheets, the PSC-Assembly and ancillary components shall be suitable for operation without damaging effect, with power supply system variations of: c. Temporary over-voltages (transient) in accordance with IEC 61439-2 Annex BB. IEC 61439-2 (2.0) Annex BB Annex BB default is : Nominal system voltage + 1200 V
Note on W11: IEC 61439-1 (2.0) 3.8.5 approximate value of voltage used to designate or identify an electrical system IEC 61439-2 (2.0) Annex BB note According to installation conditions. Max 1 000 V a.c. or 1500 V d.c.
Note on W12: S-560 (2.0) 5.2.4 PSC-Assemblies shall be type tested with co-ordinated insulation values in accordance with overvoltage category III stated in IEC 61439-1, Annex G unless defined otherwise in the Data Sheets.
Note on C13: S-560 (2.0) 5.3 : Each PSC-Assembly shall have current ratings not less than those defined in the Data Sheets at the specified upper limit ambient air temperature.
Note on Y17: IEC 61439-1 (2.0) 3.8.7 prospective short-circuit current Icp r.m.s. value of the current which would flow if the supply conductors to the circuit are shortcircuited by a conductor of negligible impedance located as near as practicable to the supply terminals of the ASSEMBLY. Comment User to define the calculated Icp and/or the User required Icw. Prospective short circuit current figure should include contributions from loads, see IEC 61439-1 (2.0) 9.3.2.
Note on Y18: IEC 61439-1 (2.0) 3.8.10.3 Rated short-time withstand current (Icw) r.m.s value of short-time current, declared by the ASSEMBLY manufacturer, that can be withstood under specified conditions, defined in terms of a current and time. IEC 61439-1 (2.0) 5.3.4 Rated short-time withstand current (Icw) (of a circuit of an ASSEMBLY) The rated short-time withstand current shall be equal to or higher than the prospective r.m.s. value of the short-circuit current (Icp) at each point of connection to the supply. Comment User to define Icw and/or Icp.
Note on Y19: IEC 61439-1 (2.0) 3.8.10.3 Rated short-time withstand current (Icw) r.m.s value of short-time current, declared by the ASSEMBLY manufacturer, that can be withstood under specified conditions, defined in terms of a current and time. IEC 61439-1 (2.0) 5.3.4 Rated short-time withstand current (Icw) (of a circuit of an ASSEMBLY) Different values of Icw for different durations (e.g. 0,2 s; 1 s; 3 s) may be assigned to an ASSEMBLY.
Note on Y20: IEC 61439-1 (2.0) Table 7 footnote Values in Table 7 represent the majority of applications. In special locations, for example in the vicinity of transformers or generators, lower values of power factor may be found, whereby the maximum prospective peak current may become the limiting value instead of the r.m.s. value of the short-circuit current. Comment Due to the vicinity of transformers, generators and the predominance of motor loads, oil and gas electrical installations often have high X/R short circuit ratios, which may require a 'n' factor greater than those in Table 7.
Note on AP20: IEC 61439-1 Table 7 : With n = 1.7
Note on AQ20: IEC 61439-1 Table 7 : With n = 2.0
Note on AR20: IEC 61439-1 Table 7 : With n = 2.0
Note on AS20: IEC 61439-1 Table 7 : With n = 2.0
Note on AT20: IEC 61439-1 Table 7 : With n = 2.1
Note on AU20: IEC 61439-1 Table 7 : With n = 2.1
Note on AV20: IEC 61439-1 Table 7 : With n = 1.7
Note on AW20: IEC 61439-1 Table 7 : With n = 2.1
Note on AX20: IEC 61439-1 Table 7 : With n = 2.2
Note on AY20: IEC 61439-1 Table 7 : With n = 2.2
Note on AZ20: IEC 61439-1 Table 7 : With n = 2.2
Note on BB20: IEC 61439-1 Table 7 : For special locations applying a factor of n = 2.5 Values of this table represent the majority of applications. In special locations, for example in the vicinity of transformers or generators, lower values of power factor may be found, whereby the maximum prospective peak current may become the limiting value instead of the r.m.s. value of the short-circuit current.
Note on BC20: IEC 61439-1 Table 7 : For special locations applying a factor of n = 2.5 Values of this table represent the majority of applications. In special locations, for example in the vicinity of transformers or generators, lower values of power factor may be found, whereby the maximum prospective peak current may become the limiting value instead of the r.m.s. value of the short-circuit current.
Note on BD20: IEC 61439-1 Table 7 : For special locations applying a factor of n = 2.5 Values of this table represent the majority of applications. In special locations, for example in the vicinity of transformers or generators, lower values of power factor may be found, whereby the maximum prospective peak current may become the limiting value instead of the r.m.s. value of the short-circuit current.
Note on BE20: IEC 61439-1 Table 7 : For special locations applying a factor of n = 2.5 Values of this table represent the majority of applications. In special locations, for example in the vicinity of transformers or generators, lower values of power factor may be found, whereby the maximum prospective peak current may become the limiting value instead of the r.m.s. value of the short-circuit current.
Note on BF20: IEC 61439-1 Table 7 : For special locations applying a factor of n = 2.5 Values of this table represent the majority of applications. In special locations, for example in the vicinity of transformers or generators, lower values of power factor may be found, whereby the maximum prospective peak current may become the limiting value instead of the r.m.s. value of the short-circuit current.
Note on BG20: IEC 61439-1 Table 7 : For special locations applying a factor of n = 2.5 Values of this table represent the majority of applications. In special locations, for example in the vicinity of transformers or generators, lower values of power factor may be found, whereby the maximum prospective peak current may become the limiting value instead of the r.m.s. value of the short-circuit current.
Note on BH20: IEC 61439-1 Table 7 : For special locations applying a factor of n = 2.5 Values of this table represent the majority of applications. In special locations, for example in the vicinity of transformers or generators, lower values of power factor may be found, whereby the maximum prospective peak current may become the limiting value instead of the r.m.s. value of the short-circuit current.
Note on BI20: IEC 61439-1 Table 7 : For special locations applying a factor of n = 2.5 Values of this table represent the majority of applications. In special locations, for example in the vicinity of transformers or generators, lower values of power factor may be found, whereby the maximum prospective peak current may become the limiting value instead of the r.m.s. value of the short-circuit current.
Note on BJ20: IEC 61439-1 Table 7 : For special locations applying a factor of n = 2.5 Values of this table represent the majority of applications. In special locations, for example in the vicinity of transformers or generators, lower values of power factor may be found, whereby the maximum prospective peak current may become the limiting value instead of the r.m.s. value of the short-circuit current.
Note on BK20: IEC 61439-1 Table 7 : For special locations applying a factor of n = 2.5 Values of this table represent the majority of applications. In special locations, for example in the vicinity of transformers or generators, lower values of power factor may be found, whereby the maximum prospective peak current may become the limiting value instead of the r.m.s. value of the short-circuit current.
Note on BL20: IEC 61439-1 Table 7 : For special locations applying a factor of n = 2.5 Values of this table represent the majority of applications. In special locations, for example in the vicinity of transformers or generators, lower values of power factor may be found, whereby the maximum prospective peak current may become the limiting value instead of the r.m.s. value of the short-circuit current.
Note on Y21: IEC 61439-2 (2.0) Annex BB Annex BB default is : Max. 60% of phase values
Note on Y22: IEC 61439-2 (2.0) Annex BB Annex BB default is : Max. 60% of phase values
Note on G24: S-560 (2.0) 5.4 A diversity factor of 1.0 shall be applied to main (horizontal) busbars. For temperature rise tests or temperature rise calculations, a diversity factor of 1.0 shall be applied for each section containing only one functional unit. The Circuit Schedule shall identify the assumed loading of the functional units. This shall be used in conjunction with IEC 61439-2, Table 101 to provide RDF for each section, and shall be subject to agreement between User and Manufacturer. The initial RDF to be applied may be defined in the Data Sheets. Spare equipped functional units and unequipped spaces for future functional units shall be considered as being loaded to 90% of their rated current and potentially rated current respectively.
Note on W25: S-560 (2.0) 5.4 A diversity factor of 1.0 shall be applied for each section containing only one functional unit. IEC 61439-2 (2.0) Table 101 IOGP comment - No RDF value given for a section containing only one functional unit.
Note on W26: S-560 (2.0) 5.4 The Circuit Schedule shall identify the assumed loading of the functional units. This shall be used in conjunction with IEC 61439-2, Table 101 to provide RDF for each section, and shall be subject to agreement between User and Manufacturer. The initial RDF to be applied may be defined in the Data Sheets. IEC 61439-2 (2.0) Table 101 Factor in the absence of an agreed value : 0.9
Note on W27: S-560 (2.0) 5.4 The Circuit Schedule shall identify the assumed loading of the functional units. This shall be used in conjunction with IEC 61439-2, Table 101 to provide RDF for each section, and shall be subject to agreement between User and Manufacturer. The initial RDF to be applied may be defined in the Data Sheets. IEC 61439-2 (2.0) Table 101 Factor in the absence of an agreed value : 0.8
Note on W28: S-560 (2.0) 5.4 The Circuit Schedule shall identify the assumed loading of the functional units. This shall be used in conjunction with IEC 61439-2, Table 101 to provide RDF for each section, and shall be subject to agreement between User and Manufacturer. The initial RDF to be applied may be defined in the Data Sheets. IEC 61439-2 (2.0) Table 101 Factor in the absence of an agreed value : 0.7
Note on W29: S-560 (2.0) 5.4 The Circuit Schedule shall identify the assumed loading of the functional units. This shall be used in conjunction with IEC 61439-2, Table 101 to provide RDF for each section, and shall be subject to agreement between User and Manufacturer. The initial RDF to be applied may be defined in the Data Sheets. IEC 61439-2 (2.0) Table 101 Factor in the absence of an agreed value : 0.6
Note on W30: S-560 (2.0) 5.4 The Circuit Schedule shall identify the assumed loading of the functional units. This shall be used in conjunction with IEC 61439-2, Table 101 to provide RDF for each section, and shall be subject to agreement between User and Manufacturer. The initial RDF to be applied may be defined in the Data Sheets. IEC 61439-2 (2.0) Table 101 Factor in the absence of an agreed value : 0.2
Note on W31: S-560 (2.0) 5.4 The Circuit Schedule shall identify the assumed loading of the functional units. This shall be used in conjunction with IEC 61439-2, Table 101 to provide RDF for each section, and shall be subject to agreement between User and Manufacturer. The initial RDF to be applied may be defined in the Data Sheets. IEC 61439-2 (2.0) Table 101 Factor in the absence of an agreed value : 0.8
Note on W32: S-560 (2.0) 5.4 The Circuit Schedule shall identify the assumed loading of the functional units. This shall be used in conjunction with IEC 61439-2, Table 101 to provide RDF for each section, and shall be subject to agreement between User and Manufacturer. The initial RDF to be applied may be defined in the Data Sheets. IEC 61439-2 (2.0) Table 101 Factor in the absence of an agreed value : 1.0
Note on V38: S-560 (2.0) 8.6.1.1 : Unless defined otherwise in the Data Sheets, the PSC-Assembly shall be arranged for a TN-S power system with separate neutral (NE) and protective (PE) bars throughtout the PSC-Assembly.
Note on V39: IEC 61439-2 (2.0) Annex BB Annex BB default is : Stationary
Note on U40: IEC 61439-2 (2.0) Annex BB Annex BB default is : Manufacturer's standard (according to application) Edit if an alternative standard is required.
Note on U41: IEC 61439-2 Annex BB Annex BB default is : Manufacturer's standard (according to application) Edit if an alternative standard is required.
Note on X44: S-560 (2.0) 6.2.1 The language used for all provided information shall be English, unless defined otherwise in the requisition or Data Sheets.
Note on U46: IEC 61439-2 (2.0) Annex BB Annex BB default is : Manufacturer's standard Edit if an alternative standard is required.
Note on U47: IEC 61439-2 (2.0) Annex BB Annex BB default is : Manufacturer's standard Edit if an alternative standard is required.
Note on U48: IEC 61439-2 (2.0) Annex BB Annex BB default is : Manufacturer's standard Edit if an alternative standard is required.
Note on X50: S-560 (2.0) 6.3 The language used on all devices, labels, plates and notices shall be English, unless alternative or additional language(s) are defined as required in the Data Sheets.
Note on X51: S-560 (2.0) 6.3 The language used on all devices, labels, plates and notices shall be English, unless alternative or additional language(s) are defined as required in the Data Sheets.
Note on X52: S-560 (2.0) 6.3.102 If defined as required in the Data Sheets, a durable mimic one-line (synoptic) diagram shall be provided on the front of the assembly, indicating the busbars, incomers, bus-couplers and main feeders. Note "If defined as required" indicates an User option. Default position is "Not required".

## Sheet 3
Row |  | Data sheets for IEC 61439 - LV Switchgear and Controlgear Assemblies | [13 empty] | Issue
2 |  | PSC-Assembly Tag No. : |  | Tag No. number here
3 |  | PSC-Assembly Service : |  | Sevice text here
4 |  | Ref. Clause | Characteristics | [5 empty] | Requirement |  |  | Additional notes
5 | 7 Service Conditions
6 |  | 7.1 Normal service conditions
7 | BB | 7.1.1, 5.6 d) | Installation location (indoor / outdoor) : | [5 empty] | Indoor | [7 empty] | Select | Indoor | Outdoor
8 | BB | 7.1.1.1 | Ambient air temperature - Lower limit : | [5 empty] | - 5 deg.C |  |  | Not exceeding this value |  |  |  |  | - 5 deg.C
9 | BB | 7.1.1.1 | Ambient air temperature - Upper limit : | [5 empty] | + 40 deg.C |  |  | Not exceeding this value |  |  |  |  | + 40 deg.C
10 | BB | 7.1.1.1 | Ambient air temperature - Daily average maximum : | [5 empty] | + 35 deg.C |  |  | Not exceeding this value |  |  |  |  | + 35 deg.C
11 | BB | 7.1.2.1 | Humidity conditions - Maximum relative humidity : | [5 empty] | 50% at + 40 deg.C | [7 empty] | 50% at + 40 deg.C
12 | BB | 7.1.3, 5.6 b) | Pollution degree (of the installation environment) : | [5 empty] | Pollution degree 3 | [7 empty] | Select | Pollution degree 1 | Pollution degree 2 | Pollution degree 3 | Pollution degree 4
13 | BB | 7.1.4 | Altitude : | [5 empty] | 2000 m |  |  | Not exceeding this value |  |  |  |  | 2000 m
14 |  | 7.2 Special service conditions
15 | BB | 7.2 a), 5.6 i) | Values different to IEC 61439 default normal service conditions : | [7 empty] | No | See values in 7.1 above |  |  |  |  | No | Yes
16 | BB | 7.2 b), 5.6 i) | Exceptional condensation liable to occur : | [7 empty] | No | [5 empty] | No | Yes
17 | BB | 7.2 c), 5.6 i) | Heavy pollution of the air by : | [7 empty] | No | [5 empty] | No | Yes
18 | BB | 7.2 d), 5.6 i) | Exposure to strong electric or magnetic fields : | [7 empty] | No | [5 empty] | No | Yes
19 | BB | 7.2 e), 5.6 i) | Exposure to extreme climatic conditions : | [7 empty] | No | [5 empty] | No | Yes
20 | BB | 7.2 f), 5.6 i) | Attack by fungus or small creatures : | [7 empty] | No | [5 empty] | No | Yes
21 | BB | 7.2 g), 5.6 i) | Installation in location where fire or explosion hazards exist : | [7 empty] | No | [5 empty] | No | Yes
22 | BB | 7.2 h), 5.6 i) | Exposure to heavy vibration, shocks, seismic occurrences : | [7 empty] | No | [5 empty] | No | Yes
23 | BB | 7.2 i), 5.6 i) | Installation where current carrying or breaking capacity is affected : | [7 empty] | No | [5 empty] | No | Yes
24 | BB | 7.2 j), 5.6 i) | Exposure to conducted and radiated disturbances : | [7 empty] | No | [5 empty] | No | Yes
25 | BB | 7.2 k), 5.6 i) | Exceptional overvoltage conditions or voltage fluctuations : | [7 empty] | No | [5 empty] | No | Yes
26 | BB | 7.2 l), 5.6 i) | Excessive harmonics in the supply voltage or load current : | [7 empty] | No | [5 empty] | No | Yes
27 |  | 7.3 Conditions during transport, storage and installation
28 | BB | 7.3 | Storage environmental conditions : |  |  | As User defined service conditions | [10 empty] | As User defined service conditions | See Requisition | See Packing Specification
29 |  | 7.3 | Heater external connection provision during storage : | [5 empty] | Select | [7 empty] | Select | Not applicable | Required | Not required
30 | 8 Constructional requirements
31 |  | 8.0.101 General
32 | BB | 8.0.101 | Construction type : |  | Floor-mounted, multi-cubicle type | [11 empty] | Select | Floor-mounted, multi-cubicle type | Wall-mounted, multi-box type
33 | BB | 8.0.101, 5.6 j) | External design type : |  | Enclosed assembly | [11 empty] | Select | Enclosed assembly | Dead-front assembly | Open-type assembly
34 |  | 8.0.101 | Mounting arrangement : |  | Longitudinal channels flush with the floor | [11 empty] | Select | Longitudinal channels flush with the floor | Directly bolted to the concrete floor | Mounted on elevated stanchions
35
36 |  | 8.0.101 | Functional unit withdrawal requirements
37 | BB | 8.5.101, 8.5.3 | Main incomers and bus couplers : |  |  |  |  | Withdrawable (W.W.W) | [8 empty] | Select | Withdrawable (W.W.W) | Disconnectable (D.D.F) | Fixed (F.F.F)
38 | BB | 8.5.101, 8.5.3 | Power feeder units rated 800 amps and above : |  |  |  |  | Withdrawable (W.W.W) | [8 empty] | Select | Withdrawable (W.W.W) | Disconnectable (D.D.F) | Fixed (F.F.F)
39 | BB | 8.5.101 | All other outgoing functional units : |  |  |  |  | Withdrawable (W.W.W) | [8 empty] | Select | Withdrawable (W.W.W) | Disconnectable (D.D.F) | Fixed (F.F.F)
40 |  | 8.0.101 | Construction for service in marine class environment : | [5 empty] | Non-marine | [7 empty] | Select | Non-marine | Marine Class
41 |  | 8.0.102 Provision for future development
42 |  | 8.0.102 | Provision of equipped spare functional outgoing units : | [5 empty] | 10% | [7 empty] | Select | None | 5% | 10% | 15% | 20% | One of each type
43 |  | 8.0.102 | Provision of space for future outgoing functional units : | [5 empty] | 10% | [7 empty] | Select | None | 5% | 10% | 15% | 20%
44 |  | 8.0.103 Technology readiness and obsolescence
45 |  | 8.0.103 | Obsolescence management plan : |  |  |  | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard | IEC 62402
46 |  | 8.1.2 Protection against corrosion
47 |  | 8.1.2 | Protection against corrosion : |  |  |  | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard
48 |  | 8.1.2 | External surface finish colour : |  |  |  | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard | RAL 7035 Light Grey
49 |  | 8.2 Degree of protection provided by an ASSEMBLY enclosure
50 | BB | 8.2.1, 5.6 k) | Minimum external mechanical impact protection : | [6 empty] | IK 08 | [6 empty] | Select | IK 07 | IK 08 | IK 09 | IK 10
51 | BB | 8.2.2, 5.6 f) | Minimum protection against ingress of solid bodies and water : | [6 empty] | IP 2X | [6 empty] | Select | IP 2X | IP 3X | IP 4X
52 |  | 8.2.2 | Section space heater requirement : | [5 empty] | Select | [7 empty] | Select | Required | Not required
53 |  |  | Heater voltage : | [5 empty] | Select | [7 empty] | Select | Not applicable | 110V ac | 220V ac | 230V ac | 240V ac
54 |  |  | Remote power source provision : |  |  |  | One for each bus section | [9 empty] | Select | Not applicable | One for each section | One for each bus section | One for the PSC-Assembly
55 |  |  | Space heater control method : | [5 empty] | Select | [7 empty] | Select | Not applicable | Thermostat | Hygrostat
56 |  | 8.2.3 / 8.2.101 PSC-ASSEMBLY with removable / withdrawable parts
57 | BB | 8.2.3 | Minimum degree of protection after removal of removable / withdrawable parts : | [7 empty] | IP 2X | [5 empty] | Select | IP 2X | IP 3X | IP 4X
58 |  | 8.2.101 | Minimum degree of protection for the external enclosure of the PSC-Assembly : | [7 empty] | IP 31 | [5 empty] | Select | IP 2X | IP 21 | IP 3X | IP 31 | IP 4X | IP 41 | IP 54 | IP 55 | IP 31 / X5
59 |  | 8.4 Protection against electric shock
60 | BB | 8.4.2, 5.6 n) | Basic protection : |  | Constructional (Manufacturer's standard) | [11 empty] | Select | Constructional (Manufacturer's standard) | Additional measures
61 | BB | 8.4.3 | Fault protection : |  |  | Automatic disconnection of supply | [10 empty] | Select | Automatic disconnection of supply | Electrical separation | Total insulation
62
|  | DOCUMENT NUMBER : |  | Data Sheet number here | [6 empty] | ISSUE : |  | XX | Sheet 3 of | 7
Note on AO3: Note : Blue cells left blank for an additional User defined pick list entry.
Note on AO4: Note : Orange cells indicate data sheet default values, to be retailed or modified by the User as required.
Note on W7: S-560 (2.0) 7.1 PSC-Assemblies shall be suitable for installation in an indoor location unless defined otherwise in the Data Sheets.
Note on W8: S-560 (2.0) 7.1.1 Ambient air temperatures as described in IEC 61439-1 shall be applied unless defined otherwise in the Data Sheets. IEC 61439-1 (2.0) defaults Indoor : -5 deg.C Outdoor : -25 deg.C Comment Modify only if site conditions are colder than the IEC default values.
Note on W9: S-560 (2.0) 7.1.1 Ambient air temperatures as described in IEC 61439-1 shall be applied unless defined otherwise in the Data Sheets. IEC 61439-1 (2.0) defaults Indoor : 40 deg.C Outdoor : 40 deg.C Comment Modify 40 deg.C value only if site conditions are higher than the IEC default value.
Note on W10: S-560 (2.0) 7.1.1 Ambient air temperatures as described in IEC 61439-1 shall be applied unless defined otherwise in the Data Sheets. IEC 61439-1 (2.0) defaults Indoor : 35 deg.C Outdoor : 35 deg.C IOGP comment Modify 35 deg.C value only if site conditions are higher than the IEC default value.
Note on W11: IEC 61439-2 (2.0) Annex BB Annex BB defaults: Indoor installations : 50 % at +40 °C. Note : Higher relative humidity may be permitted at lower temperatures, for example 90 % at +20 °C. Outdoor installations : 100 % at +25 °C. Comment Modify values only if site conditions are more onerous than the IEC default values.
Note on W12: S-560 (2.0) 7.1.3 Unless defined otherwise in the Data Sheets, PSC-Assemblies shall be suitable for use in a pollution degree 3 environment. IEC 61439-1 (2.0) extract Pollution degree 3: Conductive pollution occurs or dry, non-conductive pollution occurs which is expected to become conductive due to condensation. Unless otherwise stated, ASSEMBLIES for industrial applications are generally for use in a pollution degree 3 environment.
Note on W13: IEC 61439-2 (2.0) Annex BB Annex BB default is : Not exceeding 2000m Comment Modify 2000m value only if site elevation is higher.
Note on G15: S-560 (2.0) 7.2 Requirements for special service conditions shall be as defined in the Data Sheets.
Note on AA15: Comment Default set at "No" unless advised otherwise by the User.
Note on AA16: Comment Default set at "No" unless advised otherwise by the User.
Note on AA17: Comment Default set at "No" unless advised otherwise by the User.
Note on AA18: Comment Default set at "No" unless advised otherwise by the User.
Note on AA19: Comment Default set at "No" unless advised otherwise by the User. Where "Yes", add details in additional notes column to include temperate / desert / saline environments and UV type issues.
Note on AA20: Comment Default set at "No" unless advised otherwise by the User.
Note on AA21: Comment Default set at "No" unless advised otherwise by the User.
Note on AA22: Comment Default set at "No" unless advised otherwise by the User.
Note on AA23: Comment Default set at "No" unless advised otherwise by the User.
Note on AA24: Comment Default set at "No" unless advised otherwise by the User.
Note on AA25: Comment Default set at "No" unless advised otherwise by the User.
Note on AA26: S-560 (2.0) 7.2 l) Excessive voltage harmonics in the system greater than THD = 8%. Comment Default set at "No" unless advised otherwise by the User. Excessive is when voltage THD is greater than 8% (IEC 61000 Class 2)
Note on R28: S-560 (2.0) 7.3 Any special conditions that arise, e.g. extended storage periods, shock and vibration and / or extreme temperatures, will be stated in the Requisition. Transport packing arrangements will be provided by the Manufacturer to meet User packing and storage requirements as defined in the Requisition; this shall include weights, lifting requirements and dimensions. IEC 61439-2 (2.0) Annex BB Annex BB default is : As service conditions
Note on W29: S-560 (2.0) 7.3 Requirements for external heater supply connection during storage and transit shall be defined in the Data Sheets.
Note on Q32: S-560 (2.0) 8.0.101 PSC-Assemblies shall be fully enclosed and shall consist of multi-cubicle sections joined together to form a rigid freestanding assembly suitable for floor mounting, unless defined otherwise in the Data Sheets.
Note on Q33: S-560 (2.0) 8.0.101 PSC-Assemblies shall be fully enclosed and shall consist of multi-cubicle sections joined together to form a rigid freestanding assembly suitable for floor mounting, unless defined otherwise in the Data Sheets.
Note on Q34: S-560 (2.0) 8.0.101 PSC-Assemblies shall be suitable for securing to longitudinal runs of channels flush with the floor surface, unless defined otherwise in the Data Sheets.
Note on G36: S-560 (2.0) 8.0.101: All functional units in PSC-Assemblies shall be withdrawable, unless defined otherwise in the Data Sheets.
Note on V37: S-560 (2.0) 8.0.101 All functional units in PSC-Assemblies shall be withdrawable, unless defined otherwise in the Data Sheets. S-560 (2.0) 8.5.3 The main incomers, bus couplers, and outgoing power feeder units rated 800 amps and above shall be provided with withdrawable ACBs or non-withdrawable load switches unless defined otherwise in the Data Sheets. S-560 (2.0) 8.5.101 For withdrawable type functional units, the electrical connections shall be type (W.W.W) in accordance with IEC 61439-2. When used, for disconnectable type functional units the electrical connections shall be type (D.D.F) minimum.
Note on V38: S-560 (2.0) 8.0.101 All functional units in PSC-Assemblies shall be withdrawable, unless defined otherwise in the Data Sheets. S-560 (2.0) 8.5.3 The main incomers, bus couplers, and outgoing power feeder units rated 800 amps and above shall be provided with withdrawable ACBs or non-withdrawable load switches unless defined otherwise in the Data Sheets. S-560 (2.0) 8.5.101 For withdrawable type functional units, the electrical connections shall be type (W.W.W) in accordance with IEC 61439-2. When used, for disconnectable type functional units the electrical connections shall be type (D.D.F) minimum.
Note on V39: S-560 (2.0) 8.0.101 All functional units in PSC-Assemblies shall be withdrawable, unless defined otherwise in the Data Sheets. S-560 (2.0) 8.5.101 For withdrawable type functional units, the electrical connections shall be type (W.W.W) in accordance with IEC 61439-2. When used, for disconnectable type functional units the electrical connections shall be type (D.D.F) minimum.
Note on W40: S-560 (2.0) 8.0.101 When marine class is identified as a requirement in the Data Sheets, PSC-Assemblies shall additionally be in accordance with stated requirements for low voltage switchgear and controlgear assemblies as defined in IEC 61892-3.
Note on W42: S-560 (2.0) 8.0.102 Unless defined otherwise in the Data Sheets, PSC-Assemblies shall have the following provisions for future development: a. 10% fully equipped spare (unassigned) functional outgoing units as defined and designated in the Circuit Schedule.
Note on W43: S-560 (2.0) 8.0.102 Unless defined otherwise in the Data Sheets, PSC-Assemblies shall have the following provisions for future development: b. 10% free unequipped space provision for future functional units for outgoing circuits.
Note on U47: S-560 (2.0) 8.1.2 Unless defined otherwise in the Data Sheets, the Manufacturer’s standard painting and corrosion system can be used.
Note on U48: S-560 (2.0) 8.1.2 Manufacturers may offer their external standard surface finish colour unless specified otherwise in the Data Sheets. Comment RAL 7035 appears to be the most prevalent colour provided as a manufacturer's standard.
Note on Z50: S-560 (2.0) 8.2.1 PSC-Assemblies shall have external mechanical impact strength (IK) of minimum IK 08 as defined in IEC 62262 unless defined otherwise in the Data Sheets.
Note on AP50: IEC 62262 : Protected against 2 joules impact.
Note on AQ50: IEC 62262 : Protected against 5 joules impact.
Note on AR50: IEC 62262 : Protected against 10 joules impact.
Note on AS50: IEC 62262 : Protected against 20 joules impact.
Note on Z51: S-560 (2.0) 8.2.101 Unless defined otherwise in the Data Sheets, the minimum degree of ingress protection for the external enclosure of a PSC-Assembly shall be IP 31 for indoor use. IEC 61439-1 (2.0) 8.2.2 The degree of protection of an enclosed ASSEMBLY shall be at least IP 2X, after installation in accordance with the ASSEMBLY manufacturer's instructions.
Note on W52: S-560 (2.0) 8.2.2 PSC-Assemblies shall be provided with space heaters for anti-condensation prevention in each section, where specified in the Data Sheets.
Note on W53: S-560 (2.0) 8.2.2 Space heaters shall be designed for operation at the voltage defined in the Data Sheets.
Note on U54: S-560 (2.0) 8.2.2 The heating system of each bus section of the PSC-Assembly shall be separately supplied from a remote source unless defined otherwise in the Data Sheets and User Diagrams.
Note on W55: S-560 (2.0) 8.2.2 Each bus section heater supply shall be controlled by a thermostat/hygrostat, as defined in the Data Sheets.
Note on AA57: S-560 (2.0) 8.2.3 A minimum degree of protection of IP 2X shall be provided. S-560 (2.0) 8.2.101 When a withdrawable functional unit has been removed from a PSC-Assembly, the live parts inside the fixed compartment shall be protected against touch with a minimum degree of protection of at least IP 2X.
Note on AA58: S-560 (2.0) 8.2.101 NOTE PSC-Assembly ventilation requirements may incorporate lower levels of IP protection subject to agreement between User and Manufacturer.
Note on AX58: IOGP Comment For outdoor use: IP 31 assemblies contained within an IP X5 enclosure to meet external requirements
Note on Q60: IEC 61439-1 (2.0) 8.4.2 Basic protection can be achieved either by appropriate constructional measures on the ASSEMBLY itself or by additional measures to be taken during installation. Additional measures include use of insulation materials or barriers (8.4.2.2 / 8.4.2.3)
Note on R61: IEC 61439-2 (2.0) Annex BB Options listed in the standard : - Automatic disconnection of supply - Electrical separation - Total insulation Earthing method is defined in 8.6.1.1

## Sheet 4
Row |  | Data sheets for IEC 61439 - LV Switchgear and Controlgear Assemblies | [14 empty] | Issue
2 |  | PSC-Assembly Tag No. : |  | Tag No. number here
3 |  | PSC-Assembly Service : |  | Sevice text here
4 |  | Ref. Clause | Characteristics | [7 empty] | Requirement |  | Additional notes
5 | 8 Constructional requirements
6 |  | 8.4.6 Operating and servicing conditions
7 | BB | 8.4.6, 5.6 g) | Access to manually operated devices : | [5 empty] | Select | [8 empty] | Select | Skilled persons | Instructed persons | Ordinary persons | Authorized persons
8 |  | 8.4.6.2 | Requirements related to accessibility ;
9 | BB | 8.4.6.2.2 | for inspection and similar operations : |  |  |  | Manufacturer's standard | [10 empty] | Select | Manufacturer's standard | Additional to 8.4.6.2.2
10 | BB | 8.4.6.2.3 | for maintenance in service by authorized persons : | [6 empty] | Manufacturer's standard | [7 empty] | Select | Manufacturer's standard | Additional to 8.4.6.2.3
11 | BB | 8.4.6.2.4 | for extension in service by authorized persons : | [6 empty] | Not required | [7 empty] | Not required
12 |  | 8.4.6.2.6 | Locking arrangements
13 |  | 8.4.6.2.6 | Closed compartment doors : |  | Manufacturer's standard locking facility | [12 empty] | Select | Manufacturer's standard locking facility | Padlockable, 6mm hasp | Tumbler lock - common key | 7mm square | 8mm triangle | Double bit key No.5
14 |  | 8.4.6.2.6 | Safety shutters closed : |  | Manufacturer's standard locking facility | [12 empty] | Select | Manufacturer's standard locking facility | Padlockable, 6mm hasp
15 |  | 8.4.6.2.6 | Switches for isolating a circuit : |  | Manufacturer's standard locking facility | [12 empty] | Select | Manufacturer's standard locking facility | Padlockable, 6mm hasp
16 |  | 8.4.6.2.6 | ACBs / MCCBs in off position : |  | Manufacturer's standard locking facility | [12 empty] | Select | Manufacturer's standard locking facility | Padlockable, 6mm hasp
17 |  | 8.4.6.2.6 | Control selector switches : |  | Manufacturer's standard locking facility | [12 empty] | Select | Manufacturer's standard locking facility | Padlockable, 6mm hasp
18 |  | 8.4.6.2.6. | Padlock provider : |  | Select | [12 empty] | Select | Not applicable | User supplied | Manufacturer supplied
19 |  | 8.4.6.2.101 Operating and maintenance gangways within a PSC-ASSEMBLY
20 | BB | 8.4.6.2.101 | Gangway design and construction : | [6 empty] | Gangways not required | [7 empty] | Select | Gangways not required | Subject to agreement
21 |  | 8.5.2.101 Withdrawable parts (IEC 61439-2)
22 |  | 8.5.2.101 | Facility to remotely test withdrawn functional units | [6 empty] | Select | [7 empty] | Select | Required | Not required
23 |  | 8.5.3 Selection of switching devices and components
24 |  | 8.5.3, 9.3.2 | Incoming unit switching device requirement : |  |  |  |  | Select | [9 empty] | Select | Withdrawable ACB | Non-withdrawable load switch
25 |  | 8.5.3 | Bus coupler switching device requirement : |  |  |  |  | Select | [9 empty] | Select | Withdrawable ACB | Non-withdrawable load switch
26 |  | 8.5.3 | Outgoing power feeder units, => 800A : |  |  |  |  | Select | [9 empty] | Select | Withdrawable ACB | Non-withdrawable load switch
27 |  | 8.5.3 | Outgoing power feeder units, <= 630A : |  |  |  |  | Select | [9 empty] | Select | Fuse-Switch | MCCB
28 |  | 8.5.3 | IEC 61850 compliant IEDs | [7 empty] | Select | [6 empty] | Select | Not required | Required
29 |  | 8.5.3.103 Circuit breakers
30 |  | 8.5.3.103.1 Air circuit breakers
31 |  | 8.5.3.103.1 | Power supply for spring charging motor : | [7 empty] | Select | [6 empty] | Select | ac phase-neutral | ac line-line | 24V dc | 48V dc | 110V dc | 125V dc
32 |  | 8.5.3.103.1 | Mechanical trip facility with a transparent cover guard : | [7 empty] | Select | [6 empty] | Select | Required | Not required
33 |  | 8.5.3.103.1 | Power supply for control (tripping) : | [7 empty] | Select | [6 empty] | Select | 24V dc | 48V dc | 110V dc | 125V dc | ac line-neutral
34 |  | 8.5.3.103.1 | Power supply for control (closing) : | [7 empty] | Select | [6 empty] | Select | 24V dc | 48V dc | 110V dc | 125V dc | ac line-neutral
35 |  | 8.5.3.103.1 | Power supply for control (protection) : | [7 empty] | Select | [6 empty] | Select | 24V dc | 48V dc | 110V dc | 125V dc | ac line-neutral
36 |  | 8.5.3.103.1 | Power supply for control (indication) : | [7 empty] | Select | [6 empty] | Select | 24V dc | 48V dc | 110V dc | 125V dc | ac line-neutral
37 |  | 8.5.3.103.2 Moulded case circuit breakers
38 |  | 8.5.3.103.2 | MCCB auxiliary contact provision : |  |  | Not required | [11 empty] | Select | Not required | 1 x 52a, 1 x 52b, 1 x trip
39 |  | 8.5.3.104 Main circuit fuses
40 |  | 8.5.3.104 | Fuse system : | Select | [13 empty] | Select | Apply MCCB/MCB for main circuit protection | A - Fuses with fuse-links with blade contacts | B - Fuses with striker fuse-links with blade contacts | C - Fuse-rails | D - Fuse-bases for busbar mounting | E - Fuses with fuse-links for bolted connections | F - Fuses with fuse-links having cylindrical contact caps | G - Fuses with fuse-links with offset blade contacts | H - Fuses with fuse-links having "gD" and "gN" characteristic | I - gU fuse-links with wedge tightening contacts | J - Fuses with fuse-links having "gD class CC" and "gN class CC" characteristics | K - gK fuse-links with blade for bolted connections – High fuse-link ratings 1250A to 4800A
41 |  | 8.5.3.104 | Feeder circuit fuse utilisation category : |  |  |  |  | gG | [9 empty] | Select | gG | Not applicable (MCCB/MCB)
42 |  | 8.5.3.104 | Motor circuit fuse utilisation category : |  |  |  |  | Select | [9 empty] | Select | gG | gM | aM | Not applicable (MCCB/MCB)
43 |  | 8.5.3.105 Motor starters and contactor feeders
44 |  | 8.5.3.105 | Main circuit protection method : | [7 empty] | Select | [6 empty] | Select | Fuse protected | MCCB protected
45 |  | 8.5.3.105 | Contactor control voltage : | [7 empty] | Select | [6 empty] | Select | ac phase-neutral | ac line-line | 230V ac | 110V ac
46 |  | 8.5.3.105 | Contactor voltage source : |  |  |  | Select | [10 empty] | Select | Per functional unit | Per PSC-Assembly section
47 |  | 8.5.3.105 | Control transformer primary protection : |  |  |  | Select | [10 empty] | Select | Fuse protected | MCB protected
48 |  | 8.5.3.105 | Motor starter heater supply provision : |  |  |  | Select | [10 empty] | Select | Not required | On all motors | On motors xx kW and above | As defined in the Circuit Schedule
49 |  | 8.5.3.105 | Motor space heater supply voltage : | [7 empty] | Select | [6 empty] | Select | ac phase-neutral | ac line-line | 230V ac | 110V ac | Not applicable
50 |  | 8.5.3.105 | Earth fault front of compartment manual reset : | [7 empty] | Select | [6 empty] | Select | Not required | Required
51 |  | 8.5.3.107 Motor restarting facilities
52 |  | 8.5.3.107 | Automatic restart facility provision : |  |  |  | Not required | [10 empty] | Select | Not required | On all motors | As defined in the User Diagrams | As defined in the Circuit Schedule
53 |  | 8.5.3.110 Voltage transformers
54 |  | 8.5.3.110 | Secondary voltage : | [7 empty] | 110 V | [6 empty] | Select | 110 V | VTs not required
55 |  | 8.5.3.111 Unearthed electrical supplies
56 |  | 8.5.3.111 | Automatic earth fault location provision : |  |  |  | Select | [10 empty] | Select | Not applicable | Not required | For all individual circuits | For all outgoing individual circuits | For each section | For each bus section
57 |  | 8.5.3.111 | Provision of a portable insulation fault locator : | [7 empty] | Select | [6 empty] | Select | Not applicable | Required | Not required
58 |  | 8.5.5 Accessibility
59 | BB | 8.5.5 | Location of manually operated devices : |  |  |  | Easily accessible from the front | [10 empty] | Select | Easily accessible from the front | Easily accessible | Manufacturer's standard
60 |  | 8.5.5 | Accessibility of terminals : | [5 empty] | Manufacturer's standard | [8 empty] | Select | Manufacturer's standard | User specified
61 |  | 8.5.5 | Accessibility of indicating instruments : | [5 empty] | Manufacturer's standard | [8 empty] | Select | Manufacturer's standard | User specified
62 |  | 8.5.5 | Accessibility of operating devices : | [5 empty] | Manufacturer's standard | [8 empty] | Select | Manufacturer's standard | User specified
|  | DOCUMENT NUMBER : |  | Data Sheet number here | [7 empty] | ISSUE : |  | XX | Sheet 4 of | 7
Note on AO3: Note : Blue cells left blank for an additional User defined pick list entry.
Note on AO4: Note : Orange cells indicate data sheet default values, to be retailed or modified by the User as required.
Note on U7: IEC 61439-1 (2.0) 3.7 3.7.12 skilled person person with relevant education and experience to enable him or her to perceive risks and to avoid hazards which electricity can create 3.7.13 instructed person person adequately advised or supervised by skilled persons to enable him or her to perceive risks and to avoid hazards electricity can create 3.7.14 ordinary person person who is neither a skilled person nor an instructed person 3.7.15 authorized person skilled or instructed person, who is empowered to execute defined work IEC 61439-2 (2.0) Annex BB No default
Note on S9: IEC 61439-1 (2.0) 8.4.6.2.2 Requirements related to accessibility for inspection and similar operations The ASSEMBLY shall be constructed in such a way that certain operations, according to agreement between the ASSEMBLY manufacturer and the user, can be performed when the ASSEMBLY is in service and under voltage. Such operations may consist of: – visual inspection of • switching devices and other apparatus, • settings and indicators of relays and releases, • conductor connections and marking; – adjusting and resetting of relays, releases and electronic devices; – replacement of fuse-links; – replacement of indicating lamps; – certain fault location operations, for example voltage and current measuring with suitably designed and insulated devices.
Note on V10: IEC 61439-1 (2.0) 8.4.6.2.3 To enable maintenance as agreed upon between the ASSEMBLY manufacturer and the user on an isolated functional unit or isolated group of functional units in the ASSEMBLY, with adjacent functional units or groups still under voltage, necessary measures shall be taken. Refer to IEC 61439-2 and S-560.
Note on V11: S-560 (2.0) 8.4.6.2.4 The PSC-Assembly is not required to be extended when operating under voltage.
Note on P13: S-560 (2.0) 8.4.6.2.6 Manufacturer's standard locking provision facilities shall be provided unless defined otherwise in the Data Sheets.
Note on P14: S-560 (2.0) 8.4.6.2.6 Manufacturer's standard locking provision facilities shall be provided unless defined otherwise in the Data Sheets.
Note on P15: S-560 (2.0) 8.4.6.2.6 Manufacturer's standard locking provision facilities shall be provided unless defined otherwise in the Data Sheets.
Note on P16: S-560 (2.0) 8.4.6.2.6 Manufacturer's standard locking provision facilities shall be provided unless defined otherwise in the Data Sheets.
Note on P17: S-560 (2.0) 8.4.6.2.6 Manufacturer's standard locking provision facilities shall be provided unless defined otherwise in the Data Sheets.
Note on P18: IOGP S-560 (2.0) Manufacturer to confirm dimensions for padlock hasp as part of their data submissions irrespective of who supplies the padlocks.
Note on V20: IEC 61439-2 (2.0) 8.4.6.101 The design and construction of such gangways shall be agreed upon between ASSEMBLY manufacturer and user. Dimensions to be in excess of 1m to allow personnel access
Note on V22: S-560 (2.0) 8.5.2.101 Where defined on the Data Sheets, facilities for remote testing of withdrawable units shall be provided. This may include extension umbilicals or specific test modules. Functionality/interface of module shall be agreed between User and Manufacturer.
Note on T24: S-560 (2.0) 8.5.3 The main incomers, bus couplers, and outgoing power feeder units rated 800 amps and above shall be provided with withdrawable ACBs or non-withdrawable load switches unless defined otherwise in the Data Sheets.
Note on T25: S-560 (2.0) 8.5.3 The main incomers, bus couplers, and outgoing power feeder units rated 800 amps and above shall be provided with withdrawable ACBs or non-withdrawable load switches unless defined otherwise in the Data Sheets.
Note on T26: S-560 (2.0) 8.5.3 The main incomers, bus couplers, and outgoing power feeder units rated 800 amps and above shall be provided with withdrawable ACBs or non-withdrawable load switches unless defined otherwise in the Data Sheets.
Note on T27: S-560 (2.0) 8.5.3 The main incomers, bus couplers, and outgoing power feeder units rated 800 amps and above shall be provided with withdrawable ACBs or non-withdrawable load switches unless defined otherwise in the Data Sheets.
Note on W28: S-560 (2.0) 8.5.3 Where specified in the Data Sheets, electrical protection relays (IEDs) shall have communications protocols in compliance with IEC 61850.
Note on W31: S-560 (2.0) 8.5.3.103.1 ACB operating mechanisms shall have: d. A spring charging motor operating at phase to neutral or line-to-line voltage supply as defined in the Data Sheets.
Note on W32: S-560 (2.0) 8.5.3.103.1 ACB operating mechanisms shall have: g. A manual mechanical trip facility with a transparent cover guard and clearly labelled when defined in the Data Sheets.
Note on W33: S-560 (2.0) 8.5.3.103.1 A control power supply for tripping, closing, protection and indication functions, shall be defined in the Data Sheets.
Note on W34: S-560 (2.0) 8.5.3.103.1 A control power supply for tripping, closing, protection and indication functions, shall be defined in the Data Sheets.
Note on W35: S-560 (2.0) 8.5.3.103.1 A control power supply for tripping, closing, protection and indication, functions shall be defined in the Data Sheets.
Note on W36: S-560 (2.0) 8.5.3.103.1 A control power supply for tripping, closing, protection and indication, functions shall be defined in the Data Sheets.
Note on R38: S-560 (2.0) 8.5.3.103.2 MCCB outgoing feeder functional units (not in combination with a contactor) shall: d. Where defined in the Data Sheets, MCCBs shall be provided with a minimum of one set of auxiliary volt free contacts for trip and status indication. IOGP comment : "Where defined" implies a default position of "Not required".
Note on L40: S-560 (2.0) 8.5.3.104 Where fuses are used for main circuit protection, they shall conform to IEC 60269-1 and IEC 60269-2 and system type shall be as defined in the Data Sheets. IEC 60269-2 (5.0) 1.1 Scope Fuses for use by authorized persons are generally designed to be used in installations where the fuse-links are accessible to, and may be replaced by, authorized persons only. This standard is divided into fuse systems, each dealing with a specific example of standardized fuses for use by authorized persons: Fuse system A: Fuses with fuse-links with blade contacts (NH fuse system) Fuse system B: Fuses with striker fuse-links with blade contacts (NH fuse system) Fuse system C: Fuse-rails (NH fuse system) Fuse system D: Fuse-bases for busbar mounting (NH fuse system) Fuse system E: Fuses with fuse-links for bolted connections (BS bolted fuse system) Fuse system F: Fuses with fuse-links having cylindrical contact caps (NF cylindrical fuse system) Fuse system G: Fuses with fuse-links with offset blade contacts (BS clip-in fuse system) Fuse system H: Fuses with fuse-links having "gD" and "gN" characteristic (class J and class L time delay and non time delay fuse types) Fuse system I: gU fuse-links with wedge tightening contacts Fuse system J: Fuses with fuse-links having "gD class CC" and "gN class CC" characteristics (class CC time delay and non-time delay fuse types) Fuse system K: gK fuse-links with blade for bolted connections – High fuse-link ratings from 1 250 A up to 4 800 A (master fuse-links)
Note on T41: S-560 (2.0) 8.5.3.104 Fuses shall be high rupture capacity (HRC) type general purpose fuse links, utilization category gG for feeders and aM / gM for motor circuits to provide type 2 co-ordination, unless defined otherwise in the Data Sheets.
Note on T42: S-560 (2.0) 8.5.3.104 Fuses shall be high rupture capacity (HRC) type general purpose fuse links, utilization category gG for feeders and aM / gM for motor circuits to provide type 2 co-ordination, unless defined otherwise in the Data Sheets
Note on AR42: IEC 60269-1, 2.2.4 "a" fuse-link (partial-range breaking-capacity fuse-link, formerly back-up fuse-link) current-limiting fuse-link capable of breaking under specified conditions all currents between the lowest current indicated on its operating time-current characteristic (k2In in Figure 2) and its rated breaking capacity NOTE "a" fuse-links are generally used to provide short-circuit protection. Where protection is required against over-currents less than k2In in Figure 2, they are used in conjunction with another suitable switching device designed to interrupt such small overcurrents. IOGP Note : Type 2 co-ordination should be demonstrated with use of aM fuse links.
Note on W44: S-560 (2.0) 8.5.3.105 Motor starters and contactor feeders shall be comprised of either fuse or MCCB protected electromagnetic contactors as defined in the Data Sheets,
Note on W45: S-560 (2.0) 8.5.3.105 For PSC-Assemblies for use on 3-phase, 4-wire (TN) systems, contactors shall have an operating control voltage derived from the phase-and-neutral on the circuit (load) side of the isolating device within each functional unit, unless defined otherwise in the Data Sheets. For PSC-Assemblies for use on 3-phase, 3-wire (IT) systems, contactors shall have an operating control voltage of 230Vac unless defined otherwise in the Data Sheets,
Note on S46: S-560 (2.0) 8.5.3.105 For PSC-Assemblies for use on 3-phase, 4-wire (TN) systems, contactors shall have an operating control voltage derived from the phase-and-neutral on the circuit (load) side of the isolating device within each functional unit, unless defined otherwise in the Data Sheets. For PSC-Assemblies for use on 3-phase, 3-wire (IT) systems, contactors shall have an operating control voltage of 230Vac unless defined otherwise in the Data Sheets, derived from a control transformer, one in each section to serve all functional units in that section, unless defined otherwise in the Data Sheets.
Note on S47: S-560 (2.0) 8.5.3.105 For PSC-Assemblies for use on 3-phase, 4-wire (TN) systems, contactors shall have an operating control voltage derived from the phase-and-neutral on the circuit (load) side of the isolating device within each functional unit, unless defined otherwise in the Data Sheets. For PSC-Assemblies for use on 3-phase, 3-wire (IT) systems, contactors shall have an operating control voltage of 230Vac unless defined otherwise in the Data Sheets, derived from a control transformer, one in each section to serve all functional units in that section, unless defined otherwise in the Data Sheets.
Note on S48: S-560 (2.0) 8.5.3.105 If defined as required in the Data Sheets, motor starter functional units shall have provisions for motor space heater supply.
Note on W49: S-560 (2.0) 8.5.3.105 The motor heater supply voltage shall be as defined in the Data Sheets and shall be distributed from dedicated motor heater auxiliary bus wiring within each bus section of the PSC-Assembly.
Note on W50: S-560 (2.0) 8.5.3.105 When defined as required in the Data Sheets, earth fault protection function shall be manually reset from the front of compartment (resettable without opening the functional unit).
Note on S52: S-560 (2.0) 8.5.3.107 If defined as required in the Data Sheets, an automatic restart facility shall be provided to restart the motor after voltage dips.
Note on W54: S-560 (2.0) 8.5.3.110 VTs shall: b. Have a secondary voltage of 110 V, unless defined otherwise in the Data Sheets,
Note on S56: S-560 (2.0) 8.5.3.111 Insulation monitoring and earth fault detection shall be provided for PSC-Assemblies with unearthed electrical supplies (IT). The design and provision of such systems shall include: c. Provision for automatic location of earth faults to either individual or grouped circuits and incoming or outgoing circuit level by the use of CTs fitted in motor starters or feeders as defined in the Data Sheets,
Note on W57: S-560 (2.0) 8.5.3.111 Insulation monitoring and earth fault detection shall be provided for PSC-Assemblies with unearthed electrical supplies (IT). Where stated in the Data Sheets, provision of a portable insulation fault location system shall be provided.
Note on S59: 8.5.5 All equipment shall be accessible from the front, except for cable termination chambers, which shall be accessed from the rear or front, as defined in the Data Sheets. IEC 61439-2 (2.0) Annex BB Annex BB default is "Easily accessible". Note heights of manually operated devices to be agreed between User and Manufacturer.

## Sheet 5
Row |  | Data sheets for IEC 61439 - LV Switchgear and Controlgear Assemblies | [16 empty] | Issue
2 |  | PSC-Assembly Tag No. : |  |  | Tag No. number here
3 |  | PSC-Assembly Service : |  |  | Sevice text here
4 |  | Ref. Clause | Characteristics | [7 empty] | Requirement |  |  |  | Additional notes
5 | 8 Constructional requirements
6 |  | 8.5.5 Accessibility
7 |  | 8.5.5 | Accessibility of actuators for emergency switching : | [6 empty] | Manufacturer's standard | [9 empty] | Select | Manufacturer's standard | User specified
8 |  | 8.5.5 | Incoming unit cable termination chamber accessibility : | [7 empty] | Select | [8 empty] | Select | Front access | Rear access
9 |  | 8.5.5 | Outgoing unit cable termination chamber accessibility : | [7 empty] | Select | [8 empty] | Select | Front access | Rear access
10 |  | 8.5.5 | Door restraint | [5 empty] | Manufacturer's standard | [10 empty] | Select | Manufacturer's standard | User specified
11 |  | 8.5.5 | Maximum assembly height : | [7 empty] | Select | [8 empty] | Select | 2.5m
12 |  | 8.5.6 Barriers
13 |  | 8.5.6 | Required minimum degree of protection between -
14 |  | 8.5.6 | horizontal busbar compartments and any other compartment : | [9 empty] | IP 2X | [6 empty] | IP 2X
15 |  | 8.5.6 | incoming and bus-coupler sections ; | [9 empty] | IP 2X | [6 empty] | IP 2X
16 |  | 8.5.6 | main busbar systems of two separate sections ; | [9 empty] | IP 2X | [6 empty] | IP 2X
17 |  | 8.5.6 | panels ; | [9 empty] | IP 2X | [6 empty] | IP 2X
18 |  | 8.5.6 | compartment of each functional unit and other compartments ; | [9 empty] | IP XXB | [6 empty] | IP XXB
19 |  | 8.5.8 Indicator lights and push-buttons
20 |  | 8.5.8 | Discrete Indicator lamp type : |  |  |  | Long life LED |  |  |  | Indication colour :
21 |  | 8.5.8 | ACB / MCCB closed (on) : | [7 empty] | Red | [8 empty] | Red
22 |  | 8.5.8 | ACB / MCCB open (off) : | [7 empty] | Green | [8 empty] | Green
23 |  | 8.5.8 | ACB / MCCB tripped : | [7 empty] | Yellow | [8 empty] | Yellow
24 |  | 8.5.8 | ACB trip circuit healthy (or unhealthy) : | [7 empty] | Blue | [8 empty] | Blue
25 |  | 8.5.8 | Voltage indication (heater on) : | [7 empty] | White | [8 empty] | White
26 |  | 8.5.8 | Motor running / contactor feeder on : | [7 empty] | Red | [8 empty] | Red
27 |  | 8.5.8 | Motor stopped / contactor feeder off : | [7 empty] | Green | [8 empty] | Green
28 |  | 8.5.8 | Motor starter / contactor feeder tripped : | [7 empty] | Yellow | [8 empty] | Yellow
29 |  | 8.5.8 | Motor heater on : | [7 empty] | White | [8 empty] | White
30 |  | 8.5.9 Auxiliary components
31 |  | 8.5.9.1 General
32 |  | 8.5.9.1 | Test blocks for protection relay injection testing : | [7 empty] | Select | [8 empty] | Select | Required | Not required
33 |  | 8.5.9.2 Indicating, measuring and protection devices
34 |  | 8.5.9.2.1 | Default display type : | [6 empty] | Select | [9 empty] | Select | Digital | Analogue
35 |  | 8.5.9.2.3 | Multi-functional digital measuring device accuracy : | [6 empty] | Class 1.0 | [9 empty] | Select | Class 1.0 | Class 0,5
36 |  | 8.5.9.2.4 | Energy and maximum demand metering accuracy : | [6 empty] | Select | [9 empty] | Select | Class 1.0 | Class 0,5
37 |  | 8.5.9.2.5 | Transducer output : | [6 empty] | 4 - 20 mA | [9 empty] | Select | 4 - 20 mA | 0 -10 mA
38 |  | 8.6 Internal electrical circuits and connections
39 |  | 8.6.1 Main circuits
40 |  | 8.6.1 | Busbar insulation : | [5 empty] | Bare (uninsulated) | [10 empty] | Select | Bare (uninsulated) | Insulated
41 |  | 8.6.1 | Busbar joint plating : | [5 empty] | Manufacturer's standard (plated) | [10 empty] | Select | Bare (unplated) | Manufacturer's standard (plated)
42 |  | 8.6.1.1 Neutral
43 | BB | 8.6.1.1 | System earthing method : | [7 empty] | TN-S | [8 empty] | Select | IT | TN-C | TN-C-S | TN-S | TT
44 |  | 8.6.1.1 | Main earth-neutral link position : |  |  |  |  | N-PE link at each incomer unit | [11 empty] | Select | N-PE link at each incomer unit | N-PE link at each transformer
45 |  | 8.6.1.1 | Ratio of cross section of the neutral conductor to phase conductors ;
46 | BB | 8.6.1.1 |  | phase conductors up to and including 16mm2 : | [6 empty] | 100 % | [8 empty] | 100 %
47 | BB | 8.6.1.1 |  | phase conductors above 16mm2 : | [6 empty] | 50 % (min. 16 mm2) | [8 empty] | 50 % (min. 16 mm2)
48 |  | 8.6.1.2 Earth bar
49 |  | 8.6.1.2 | Supplementary bonding for extraneous conductive parts : | [7 empty] | Select | [8 empty] | Select | 2.5 mm2 | 4 mm2 | 6 mm2 | Manufacturer's standard
50 |  | 8.6.2 Auxiliary circuits
51 |  | 8.6.2 | Resistance to abnormal heat and fire : | [5 empty] | Low smoke, zero halogen | [10 empty] | Select | Low smoke, zero halogen | Manufacturer's standard
52 |  | 8.6.5 Identification of the conductors of main and auxiliary circuits :
53 |  | 8.6.5 | Phase 1 |  |  | L1 | [5 empty] | Brown | [7 empty] | L1 | Brown
54 |  | 8.6.5 | Phase 2 |  |  | L2 | [5 empty] | Black | [7 empty] | L2 | Black
55 |  | 8.6.5 | Phase 3 |  |  | L3 | [5 empty] | Grey | [7 empty] | L3 | Grey
56 |  | 8.6.5 | Neutral |  |  | N | [5 empty] | (Light) Blue | [7 empty] | N | (Light) Blue
57 |  | 8.6.5 | Protective earth |  |  | PE and/or earth symbol | [5 empty] | Yellow/Green | [7 empty] | PE and/or earth symbol | Yellow/Green
58 |  | 8.6.5 | DC positive pole |  |  | ( + ) | [5 empty] | Red | [7 empty] | ( + ) | Red
59 |  | 8.6.5 | DC negative pole |  |  | ( - ) | [5 empty] | Black | [7 empty] | ( - ) | Black
60
61
62
|  | DOCUMENT NUMBER : |  |  | Data Sheet number here | [8 empty] | ISSUE : |  | XX | Sheet 5 of | 7
Note on AO3: Note : Blue cells left blank for an additional User defined pick list entry.
Note on AO4: Note : Orange cells indicate data sheet default values, to be retailed or modified by the User as required.
Note on W8: S-560 (2.0) 8.5.5 All equipment shall be accessible from the front, except for cable termination chambers, which shall be accessed from the rear or front, as defined in the Data Sheets.
Note on W9: S-560 (2.0) 8.5.5 All equipment shall be accessible from the front, except for cable termination chambers, which shall be accessed from the rear or front, as defined in the Data Sheets.
Note on T10: S-560 (2.0): Door restraints shall be provided for securing doors in the open position in the following cases: a. When placed on floating offshore installations, b. When located outdoors (exposed to wind), c. When door is equipped with electrical components.
Note on W11: S-560 (2.0) 8.5.5 NOTE In some countries, national codes or regulations may further limit the minimum and maximum height. Unless defined otherwise in the Data Sheets, PSC-Assembly height will be a maximum of 2.5m. Comment The 2.5m height is also intended to align with a maximum handling height of 2.7m, allowing 150mm below and 50mm clearance above.
Note on Z14: S-560 (2.0) 8.5.6 PSC-Assemblies shall be built with metallic or non-metallic internal barriers to achieve the required form of segregation and shall provide the following minimum degrees of protection unless defined otherwise in the Data Sheets: Between horizontal busbar compartments and any other compartment - IP 2X
Note on Z15: S-560 (2.0) 8.5.6 PSC-Assemblies shall be built with metallic or non-metallic internal barriers to achieve the required form of segregation and shall provide the following minimum degrees of protection unless defined otherwise in the Data Sheets: Between incoming and bus-coupler sections - IP 2X
Note on Z16: S-560 (2.0) 8.5.6 PSC-Assemblies shall be built with metallic or non-metallic internal barriers to achieve the required form of segregation and shall provide the following minimum degrees of protection unless defined otherwise in the Data Sheets: Between main busbar systems of two separate sections - IP 2X
Note on Z17: S-560 (2.0) 8.5.6 PSC-Assemblies shall be built with metallic or non-metallic internal barriers to achieve the required form of segregation and shall provide the following minimum degrees of protection unless defined otherwise in the Data Sheets: Between panels - IP 2X
Note on Z18: S-560 (2.0) 8.5.6 PSC-Assemblies shall be built with metallic or non-metallic internal barriers to achieve the required form of segregation and shall provide the following minimum degrees of protection unless defined otherwise in the Data Sheets: Between compartments of each functional unit and other compartments - IP XXB
Note on W20: S-560 (2.0) 8.5.8 Indicator light colour coding shall be in accordance with IEC 60073 and the illustrative table below unless defined otherwise in the Data Sheets:
Note on W32: S-560 (2.0) 8.5.9.1 Where defined in the Data Sheets, test blocks for protection relay secondary injection testing shall be provided to allow relay testing and calibration from the front of the panel without disconnecting wiring.
Note on V34: S-560 (2.0) 8.5.9.2.1 Indicating instruments shall be digital or analogue type as defined in the Data Sheets and shall have minimum accuracy class of 2.5.
Note on V35: S-560 (2.0) 8.5.9.2.3 Multi-functional digital measuring devices shall have an accuracy class of 1.0 unless defined otherwise in the Data Sheets
Note on V36: S-560 (2.0) 8.5.9.2.4 Energy meters and maximum demand meters shall be in accordance with IEC 62052-11 with a default minimum accuracy class as defined in the Data Sheets or higher accuracy for specific schemes as defined in the User Diagrams….
Note on V37: S-560 (2.0) 8.5.9.2.5 Unless defined otherwise in the Data Sheets, the transducer outputs shall be 4-20 mA.
Note on T40: S-560 (2.0) 8.6.1 The main and interconnecting busbars, phase and neutral, and joints shall be bare (uninsulated) unless defined otherwise in the Data Sheets.
Note on T41: Comment Default set at Bare (unplated). Specification S-560 (2.0) has no stated position on busbar joint treatments. Manufacturer default is usually bare unless supplementary plating is defined as required by the User.
Note on W43: S-560 (2.0) 8.6.1.1 Unless defined otherwise in the Data Sheets, the PSC-Assembly shall be arranged for a TN-S power system with separate neutral (NE) and protective (PE) bars throughout the PSC-Assembly.
Note on S44: S-560 (2.0) 8.6.1.1 Unless defined otherwise in the Data Sheets, for a TN-S system, each incoming circuit (downstream of the transformer) shall be provided with a removable link between the neutral and the PE bar at the PSC-Assembly.
Note on W46: IEC 61439-2 (2.0) Annex BB Cell pre-populated with IEC 61439-2 Annex BB default of "100%"
Note on W47: IEC 61439-2 (2.0) Annex BB Cell pre-populated with IEC 61439-2 Annex BB default of "50% (min. 16 mm 2)"
Note on W49: S-560 (2.0) 8.6.1.2 Doors and hinged parts shall be bonded to the assembly structure by means of a flexible copper connection having a minimum cross-sectional area as defined in the Data Sheets dependent on the rated short circuit level, Manufacturer's standard should selected. General reference to IEC 60364-4-41, 415.2 and IEC 60439-0, 7.1.
Note on T51: S-560 (2.0) 8.6.2 Main / Auxiliary circuits within the PSC-Assembly shall be low smoke, zero halogen content unless otherwise defined in the Data Sheets.
Note on P53: S-560 (2.0) 8.6.5 The identification of the conductors of main and auxiliary circuits shall be as follows unless defined otherwise in the Data Sheets : AC Circuits, Phase 1 - L1 - Brown
Note on P54: S-560 (2.0) 8.6.5 The identification of the conductors of main and auxiliary circuits shall be as follows unless defined otherwise in the Data Sheets : AC Circuits, Phase 2 - L2 - Black
Note on P55: S-560 (2.0) 8.6.5 The identification of the conductors of main and auxiliary circuits shall be as follows unless defined otherwise in the Data Sheets : AC Circuits, Phase 3 - L3 - Grey
Note on P56: S-560 (2.0) 8.6.5 The identification of the conductors of main and auxiliary circuits shall be as follows unless defined otherwise in the Data Sheets : AC Circuits, Neutral - N - (Light) Blue
Note on P57: S-560 (2.0) 8.6.5 The identification of the conductors of main and auxiliary circuits shall be as follows unless defined otherwise in the Data Sheets : AC Circuits, Protective earth - PE and/or earth symbol - Yellow/Green
Note on P58: S-560 (2.0) 8.6.5 The identification of the conductors of main and auxiliary circuits shall be as follows unless defined otherwise in the Data Sheets : DC Circuits, Positive pole (+) - Red
Note on P59: S-560 (2.0) 8.6.5 The identification of the conductors of main and auxiliary circuits shall be as follows unless defined otherwise in the Data Sheets : DC Circuits, Negative pole (-) - Black

## Sheet 6
Row |  | Data sheets for IEC 61439 - LV Switchgear and Controlgear Assemblies | [13 empty] | Issue
2 |  | PSC-Assembly Tag No. : |  |  | Tag No. number here
3 |  | PSC-Assembly Service : |  |  | Sevice text here
4 |  | Ref. Clause | Characteristics | [6 empty] | Requirement |  | Additional notes
5 | 8 Constructional requirements
6 |  | 8.8 Terminals for external conductors
7 | BB | 8.8 | Incoming (supply) unit direction of external conductors : | [6 empty] | From below | [6 empty] | Select | From below | From above
8 | BB | 8.8 | Incoming (supply) unit external conductor type : | [6 empty] | Cable | [6 empty] | Select | Cable | Busbar Trunking System
9 | BB | 8.8 | Outgoing (load) unit direction of external conductors : | [6 empty] | From below | [6 empty] | Select | From below | From above
10 | BB | 8.8 | Outgoing (load) unit external conductor type : | [6 empty] | Cable | [6 empty] | Select | Cable
11 | BB | 8.8 | Auxiliary cable direction of external conductors : | [6 empty] | From below | [6 empty] | Select | From below | From above
12 | BB | 8.8 | Auxiliary cable external conductor type : | [6 empty] | Cable | [6 empty] | Select | Cable
13 | BB | 8.8 | External conductor material : | [6 empty] | Copper | [6 empty] | Select | Copper | Aluminium
14 | BB | 8.8 | External phase conductor, cross sections : |  |  |  |  | See Circuit Schedule | [8 empty] | Select | See Circuit Schedule | To IEC 61439-1 Table A.1 | Subject to agreement
15 | BB | 8.8 | External PE, N, PEN conductors : |  |  |  |  | As IEC 61439-1 Clause 8.8 | [8 empty] | As IEC 61439-1 Clause 8.8
16 | BB | 8.8 | Special terminal identification requirements : |  |  |  |  | Manufacturer's standard |  |  |  | To meet User 8.6.5 requirements |  |  |  |  | Manufacturer's standard
17 |  | 8.8 | Cable penetration method |  |  | Gland plate | [10 empty] | Select | Gland plate | Transit Arrangement | No gland plate
18 |  | 8.8 | Gland plate material type : |  |  | Removable, undrilled, steel | [10 empty] | Select | Removable, undrilled, non-magnetic | Removable, undrilled, aluminium, | Removable, undrilled, steel | Transit Arrangement
19 |  | 8.8 | Single core cable gland plate type : |  |  | Removable, undrilled, non-magnetic | [10 empty] | Select | Removable, undrilled, non-magnetic | Transit Arrangement
20 |  | 8.8 | Glanding arrangement : |  |  | Select | [10 empty] | Select | Transit Arrangement | No special gland requirements | Insulated glands
21 |  | 8.8 | Large incomer/feeder entry method : |  |  | Select | [10 empty] | Select | Bottom located, direct entry permitted | Top located, direct entry permitted
22 |  | 8.8.1 Terminals for control and auxiliaries
23 |  | 8.8.1 | Spare terminal provision for future use : | [6 empty] | 10% | [6 empty] | Select | None | 10% | 20%
24 |  | 8.101 Internal separation of PSC-ASSEMBLIES (IEC 61439-2)
25 | BB | 8.101 | Internal separation for ACB functional units : | [6 empty] | Select | [6 empty] | Select | Form 3b | Form 4a | Form 4b |  | Form 3 Type 2 | Form 4 Type 1 | Form 4 Type 2 | Form 4 Type 3 | Form 4 Type 4 | Form 4 Type 5 | Form 4 Type 6 | Form 4 Type 7
26 | BB | 8.101 | Internal separation for non-ACB functional units : | [6 empty] | Select | [6 empty] | Select | Form 3b | Form 4a | Form 4b |  | Form 3 Type 2 | Form 4 Type 1 | Form 4 Type 2 | Form 4 Type 3 | Form 4 Type 4 | Form 4 Type 5 | Form 4 Type 6 | Form 4 Type 7
27 | 9 Performance requirements
28 |  | 9.3 Short-circuit protection and short-circuit withstand strength
29 |  | 9.3.1 General
30 |  | 9.3.1 | IEC TR 61641 Arcing Class :
31 |  | 9.3.1 |  | Busbar section | [5 empty] | Select | [6 empty] | Select | Arcing Class A | Arcing Class B | Arcing Class C | Arcing Class I
32 |  | 9.3.1 |  | ACB functional units | [5 empty] | Select | [6 empty] | Select | Arcing Class A | Arcing Class B | Arcing Class C | Arcing Class I
33 |  | 9.3.1 |  | Non-ACB functional units | [5 empty] | Select | [6 empty] | Select | Arcing Class A | Arcing Class B | Arcing Class C | Arcing Class I
34 |  | 9.3.1 | Busbar section IEC TR 61641 requirement -
35 |  | 9.3.1 | Busbar section under arcing conditions (Ip arc) : | [6 empty] | Input value | [6 empty] | Input value
36 |  | 9.3.1 | Busbar arc duration withstand (tarc) : | [6 empty] | Select | [6 empty] | Select | Not applicable | 0.3 seconds
37 |  | 9.3.1 | Busbar section under self-extinguishing arcing conditions (Ips arc) : | [6 empty] | Input value | [6 empty] | Input value
38 |  | 9.3.1 | ACB section IEC TR 61641 requirement -
39 |  | 9.3.1 | ACB functional units under arcing conditions (Ip arc) : | [6 empty] | Input value | [6 empty] | Input value
40 |  | 9.3.1 | ACB arc duration withstand (tarc) : | [6 empty] | Select | [6 empty] | Select | Not applicable | 0.3 seconds
41 |  | 9.3.1 | ACB under self-extinguishing arcing conditions (Ips arc) : | [6 empty] | Input value | [6 empty] | Input value
42 |  | 9.3.1 | Non-ACB section IEC TR 61641 requirement -
43 |  | 9.3.1 | Non-ACB functional units under arcing conditions (Ip arc) : | [6 empty] | Input value | [6 empty] | Input value
44 |  | 9.3.1 | Non-ACB arc duration withstand (tarc) : | [6 empty] | Select | [6 empty] | Select | Not applicable | 0.3 seconds
45 |  | 9.3.1 | Non-ACB under self-extinguishing arcing conditions (Ips arc) : | [6 empty] | Input value | [6 empty] | Input value
46 |  | 9.3.1 | Integrated internal arc fault detection system : | [6 empty] | Not required | [6 empty] | Select | Not required | Required
47 |  | 9.3.2 Information concerning short-circuit withstand strength
48 | BB | 9.3.2 | SCPD in the incoming functional unit requirement : | [5 empty] | See S-560 8.5.3 | [7 empty] | See S-560 8.5.3
49 | BB | 9.3.2 | Loads likely to contribute to the short circuit current : | [5 empty] | See Circuit Schedule | [7 empty] | See Circuit Schedule
50 |  | 9.3.4 Co-ordination of protective devices
51 | BB | 9.3.4 | Co-ordination of short circuit protection device details : | [5 empty] | Select | [7 empty] | Select | No requirement | See Circuit Schedule
52 |  | 9.4 Electromagnetic Compatibility (EMC) Environment
53 | BB | 9.4, 5.6 h) | EMC Environment : | [6 empty] | A | [6 empty] | Select | A | B
54 | 10 Design verification
55 | BB | 10.2.2.2 & 3 | Resistance to corrosion, severity test : |  |  |  | Indoor Location Severity test A | [9 empty] | Select | Indoor Location - Severity test A | Outdoor Location - Severity test B
56 | BB | 10.2.4, 7.2 e) | Resistance to ultra-violet (UV) radiation : |  |  |  | Indoor : Not applicable | [9 empty] | Select | Indoor : Not applicable | Outdoor : Add specific requirements
57
58 | 11 Routine verification
59 | BB | 11.101 | Additional on site testing requirements : |  |  |  | See Inspection & Test Plan (ITP) | [9 empty] | Select | See Inspection & Test Plan (ITP) | Manufacturer's standard
60
61
62
|  | DOCUMENT NUMBER : |  |  | Data Sheet number here | [5 empty] | ISSUE : |  | XX | Sheet 6 of | 7
Note on AO3: IOGP Note : Blue cells left blank for an additional User defined pick list entry.
Note on AO4: IOGP Note : Orange cells indicate data sheet default values, to be retailed or modified by the User as required.
Note on W7: S-560 (2.0) 8.8 All power (supply & load), and auxiliary cables shall enter from below unless defined otherwise for a PSC-Assembly in the Data Sheets, or defined otherwise for individual circuits in the Circuit Schedule.
Note on W8: Comment Default set as Cable. S-560 (2.0) 8.8 presumes cables.
Note on W9: S-560 (2.0) 8.8 All power (supply & load), and auxiliary cables shall enter from below unless defined otherwise for a PSC-Assembly in the Data Sheets, or defined otherwise for individual circuits in the Circuit Schedule.
Note on W10: Comment Default set as Cable. S-560 (2.0) 8.8 presumes cables.
Note on W11: S-560 (2.0) 8.8 All All power (supply & load), and auxiliary cables shall enter from below unless defined otherwise for a PSC-Assembly in the Data Sheets, or defined otherwise for individual circuits in the Circuit Schedule.
Note on W12: Comment Default set as Cable. S-560 (2.0) 8.8 presumes cables.
Note on W13: IEC 61439-2 (2.0) Annex BB Cell pre-populated with IEC 61439-2 Annex BB default of "Copper".
Note on T14: S-560 (2.0) 8.8 Terminals, both main and auxiliary, cable entries, support facilities for cable clamping, and earthing facilities shall be provided, suitable for the type, size and number of cables as defined in the Circuit Schedule. In the absence of User defined field cable information, guidance shall be taken from IEC 61439-1 Annex A Table A.1, using maximum cross-section values.
Note on T15: IEC 61439-2 (2.0) Annex BB Annex BB default is : "As defined within the standard" Cell pre-populated with "As IEC 61439-1 Clause 8.8"
Note on T16: IEC 61439-2 (2.0) Annex BB Annex BB default is : "Manufacturer's standard" Edit if User alternative is required.
Note on R17: S-560 (2.0) 8.8 Unless defined otherwise in the Data Sheets, removable, undrilled steel (non-magnetic) gland plates shall be provided in each vertical panel for glanding of power and control cables.
Note on R18: S-560 (2.0) 8.8 Unless defined otherwise in the Data Sheets, removable, undrilled steel (non-magnetic) gland plates shall be provided in each vertical panel for glanding of power and control cables.
Note on R19: S-560 (2.0) 8.8 Unless defined otherwise in the Data Sheets, removable, undrilled steel (non-magnetic) gland plates shall be provided in each vertical panel for glanding of power and control cables.
Note on R20: S-560 (2.0) 8.8 In the case of single core cables with armour and/or lead sheathing, any requirement for special glands which allow for insulation between the armour/lead sheath and gland plate shall be defined in the Data Sheets.
Note on R21: S-560 (2.0) 8.8 Where defined in the Data Sheets, large incomers/feeders shall be located at bottom of the PSC section and have provision for direct entry and termination.
Note on W23: S-560 (2.0) 8.8.1 Unless specified otherwise in the Data Sheets, space for not less than 10% spare terminals shall be provided for future use.
Note on W25: S-560 (2.0) 8.101 Unless defined otherwise in the Data Sheets, form of internal separation shall be a minimum of Form 4a for ACBs and a minimum of Form 3b for all other functional units. Options for internal separation can include those detailed in BS EN 61439-1 and BS EN 61439-2.
Note on AP25: IEC 61439-2 Annex AA : Form 3b Separation of busbars from all functional units + Separation of all functional units from one another + Separation of terminals for external conductors and external conductors from the functional units, but not from the terminals of other functional units + Terminals and external conductors separated from busbars.
Note on AQ25: IEC 61439-2 Annex AA : Form 4a Separation of busbars from all functional units + Separation of all functional units from one another + Separation of terminals for external conductors associated with a functional unit from the terminals of any other functional unit and the busbars + Separation of the external conductors from the busbars + Separation of the external conductors associated with a functional unit from other functional units and their terminals + External conductors need not be separated from each other + Terminals in same compartment as associated functional unit.
Note on AR25: IEC 61439-2 Annex AA : Form 4b Separation of busbars from all functional units + Separation of all functional units from one another + Separation of terminals for external conductors associated with a functional unit from the terminals of any other functional unit and the busbars + Separation of the external conductors from the busbars + Separation of the external conductors associated with a functional unit from other functional units and their terminals + External conductors need not be separated from each other + Terminals not in same compartment as associated functional unit.
Note on AT25: IOGP S-560 (1.0) 8.101 NOTE 3 Options for internal separation can include those detailed in BS EN 61439-1 and BS EN 61439-2 and defined in the Data Sheets.
Note on W26: S-560 (2.0) 8.101 Unless defined otherwise in the Data Sheets, form of internal separation shall be a minimum of Form 4a for ACBs and a minimum of Form 3b for all other functional units. Options for internal separation can include those detailed in BS EN 61439-1 and BS EN 61439-2.
Note on AP26: IEC 61439-2 Annex AA : Form 3b Separation of busbars from all functional units + Separation of all functional units from one another + Separation of terminals for external conductors and external conductors from the functional units, but not from the terminals of other functional units + Terminals and external conductors separated from busbars.
Note on AQ26: IEC 61439-2 Annex AA : Form 4a Separation of busbars from all functional units + Separation of all functional units from one another + Separation of terminals for external conductors associated with a functional unit from the terminals of any other functional unit and the busbars + Separation of the external conductors from the busbars + Separation of the external conductors associated with a functional unit from other functional units and their terminals + External conductors need not be separated from each other + Terminals in same compartment as associated functional unit.
Note on AR26: IEC 61439-2 Annex AA : Form 4b Separation of busbars from all functional units + Separation of all functional units from one another + Separation of terminals for external conductors associated with a functional unit from the terminals of any other functional unit and the busbars + Separation of the external conductors from the busbars + Separation of the external conductors associated with a functional unit from other functional units and their terminals + External conductors need not be separated from each other + Terminals not in same compartment as associated functional unit.
Note on AT26: IOGP S-560 (1.0) 8.101 NOTE 3 Options for internal separation can include those detailed in BS EN 61439-1 and BS EN 61439-2 and defined in the Data Sheets.
Note on W30: S-560 (2.0) 9.3.1 The PSC-Assembly shall be designed, constructed and type tested (as a special test) for “Internal Arc Containment” in accordance with the requirements of IEC TR 61641. The minimum requirement is for Arcing Class A.
Note on W31: S-560 (2.0) 9.3.1 The PSC-Assembly shall be designed, constructed and type tested (as a special test) for “Internal Arc Containment” in accordance with the requirements of IEC TR 61641. The minimum requirement is for Arcing Class A.
Note on W32: S-560 (2.0) 9.3.1 The PSC-Assembly shall be designed, constructed and type tested (as a special test) for “Internal Arc Containment” in accordance with the requirements of IEC TR 61641. The minimum requirement is for Arcing Class A.
Note on W33: S-560 (2.0) 9.3.1 The PSC-Assembly shall be designed, constructed and type tested (as a special test) for “Internal Arc Containment” in accordance with the requirements of IEC TR 61641. The minimum requirement is for Arcing Class A.
Note on W35: S-560 (2.0) 9.3.1 Where Arcing Class B and Arc Class C assemblies are defined, the PSC-Assembly shall withstand internal arcing for 0.3 s. Ip arc and Ips arc shall be defined in the Data Sheets.
Note on W36: S-560 (2.0) 9.3.1 Where Arcing Class B and Arc Class C assemblies are defined, the PSC-Assembly shall withstand internal arcing for 0.3 s. Ip arc and Ips arc shall be defined in the Data Sheets.
Note on W37: S-560 (2.0) 9.3.1 Where Arcing Class B and Arc Class C assemblies are defined, the PSC-Assembly shall withstand internal arcing for 0.3 s. Ip arc and Ips arc shall be defined in the Data Sheets.
Note on W39: S-560 (2.0) 9.3.1 Where Arcing Class B and Arc Class C assemblies are defined, the PSC-Assembly shall withstand internal arcing for 0.3 s. Ip arc and Ips arc shall be defined in the Data Sheets.
Note on W40: S-560 (2.0) 9.3.1 Where Arcing Class B and Arc Class C assemblies are defined, the PSC-Assembly shall withstand internal arcing for 0.3 s. Ip arc and Ips arc shall be defined in the Data Sheets.
Note on W41: S-560 (2.0) 9.3.1 Where Arcing Class B and Arc Class C assemblies are defined, the PSC-Assembly shall withstand internal arcing for 0.3 s. Ip arc and Ips arc shall be defined in the Data Sheets.
Note on W43: S-560 (2.0) 9.3.1 Where Arcing Class B and Arc Class C assemblies are defined, the PSC-Assembly shall withstand internal arcing for 0.3 s. Ip arc and Ips arc shall be defined in the Data Sheets.
Note on W44: S-560 (2.0) 9.3.1 Where Arcing Class B and Arc Class C assemblies are defined, the PSC-Assembly shall withstand internal arcing for 0.3 s. Ip arc and Ips arc shall be defined in the Data Sheets.
Note on W45: S-560 (2.0) 9.3.1 Where Arcing Class B and Arc Class C assemblies are defined, the PSC-Assembly shall withstand internal arcing for 0.3 s. Ip arc and Ips arc shall be defined in the Data Sheets.
Note on W46: S-560 (2.0) 9.3.3 Where defined as required in the Data Sheets, an internal arc fault detection system shall be provided and integrated into the PSC-Assembly.
Note on V48: IEC 61439-1 (2.0) 9.3.2 For ASSEMBLIES with a short-circuit protective device (SCPD) incorporated in the incoming unit.... S-560 (2.0) 8.5.3 The main incomers, bus couplers, and outgoing power feeder units rated 800 amps and above shall be provided with withdrawable ACBs or non-withdrawable load switches unless defined otherwise in the Data Sheets.
Note on V49: IEC 61439-1 (2.0) 9.3.2 For an ASSEMBLY having several incoming units which are likely to be in operation simultaneously, and for an ASSEMBLY having one incoming unit and one or more outgoing high-power units likely to contribute to the short-circuit current, it is necessary to determine the values of the prospective short-circuit current in each incoming unit, in each outgoing unit and in the busbars based on data provided by the user.
Note on V51: IEC 61439-1 (2.0) 9.3.4 The co-ordination of protective devices within the ASSEMBLY with those to be used external to the ASSEMBLY shall be the subject of an agreement between the ASSEMBLY manufacturer and the user.
Note on W53: IEC 61439-1 (2.0) Annex J Environment A: relates to a power network supplied from a high or medium voltage transformer dedicated to the supply of an installation feeding manufacturing or similar plant, and intended to operate in or in proximity to industrial locations. Environment B: relates to low-voltage public mains networks or apparatus connected to a dedicated DC source which is intended to interface between the apparatus and the low-voltage public mains network.
Note on B54: IOGP S-560 (1.0) 10.1 General Additional design verification shall be carried out in accordance with the requirements defined in this Specification and Data Sheets. Performance test requirements should be detailed in the Requisition eg performance verification (type) testing of switchboards or individual tiers.
Note on S56: S-560 (2.0) Refer to climatic conditions detailed in 7.2e) and provide sufficient information to Manufacturer to ensure equipment is suitable for the environment.

## Sheet 7
Row | Note | Data sheets for IEC 61439 - LV Switchgear and Controlgear Assemblies | [6 empty] | Issue
2
3 |  | PSC-Assembly Tag No. : |  | Tag No. number here
4 |  | PSC-Assembly Service : |  | Sevice text here
5
6 | USER SUPPLEMENTARY REQUIREMENTS
7 |  |  | Delete this sheet if not required.
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
|  | DOCUMENT NUMBER : |  | Data Sheet number here | ISSUE : | XX | Sheet 7 of | 7